###### SALIENT DETAILS

| Name of Scheme |  | Providing CWSS to Melur, Avaniapuram, Thirumangalam Municipalities, A.Vellalapatti, Vilangudi, Paravai, Thirunagar, Alanganallur, Palamedu Town Panchayats and 1,430 Rural Habitations in 8 Unions in Madurai District and Singampuneri Town Panchayat in Sivagangai District. |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| A.S.No & Amount |  | G.O.Ms.No.164/MA & WS/Dt.11.08.2010 for Rs.784.00Crore. |  |  |  |  |  |  |  |
| T.S.No & Amount |  | C.E/SR/NO 75 /Dt. 27.12.2010 for Rs.780.50Crore. |  |  |  |  |  |  |  |
| A.M.Cost |  | Rs.15.87 Crore |  |  |  |  |  |  |  |
| Per capita cost |  | Rs.6,021/- |  |  |  |  |  |  |  |
| Cost per 1000 litres |  | Rs.19.56 |  |  |  |  |  |  |  |
| Prportionate installation Cost& AM cost |  | Name of Beneficiary |  | Installation Cost (Rs. in Crore) |  |  |  | A. M. Cost (Rs. in Crore) |  |
|  |  | Melur Mpty |  | 23.70 |  |  |  | 0.56 |  |
|  |  | Avaniapuram Mpty |  | 60.64 |  |  |  | 1.24 |  |
|  |  | Thirumangalam Mpty |  | 67.82 |  |  |  | 1.63 |  |
|  |  | A.Vellapatty TP |  | 3.26 |  |  |  | 0.07 |  |
|  |  | Thirunagar TP |  | 15.04 |  |  |  | 0.34 |  |
|  |  | Paravai TP |  | 26.02 |  |  |  | 0.55 |  |
|  |  | Vilangudi TP |  | 30.84 |  |  |  | 0.67 |  |
|  |  | Alanganallur TP |  | 6.10 |  |  |  | 0.15 |  |
|  |  | Palamedu TP |  | 7.18 |  |  |  | 0.14 |  |
|  |  | Singampunari TP |  | 15.76 |  |  |  | 0.31 |  |
|  |  | 1,430 Rural Habitations |  | 474.99 |  |  |  | 9.10 |  |
|  |  | Industries |  | 49.15 |  |  |  | 1.11 |  |
|  |  | ###### Total |  | 780.50 |  |  |  | 15.87 |  |
| POPULATION AND REQUIREMENT |  | Base Year (2012) |  | Intermediate (2027) |  |  |  | Ultimate (2042) |  |
| Population |  |  |  |  |  |  |  |  |  |
| MELUR |  | 39,120 |  | 46,265 |  |  |  | 53,409 |  |
| AVANIAPURAM |  | 64,383 |  | 85,589 |  |  |  | 1,11,131 |  |
| THIRUMANGALAM |  | 56,366 |  | 78,611 |  |  |  | 1,09,635 |  |
| SUB TOTAL A |  | 1,59,869 |  | 2,10,465 |  |  |  | 2,74,175 |  |
| THIRUNAGAR |  | 19,379 |  | 24,605 |  |  |  | 29,830 |  |
| PARAVAI |  | 21,202 |  | 29,316 |  |  |  | 40,536 |  |
| VILANGUDI |  | 27,594 |  | 38,730 |  |  |  | 52,605 |  |
| A.VELLALAPATTY |  | 7,585 |  | 8,254 |  |  |  | 8,913 |  |
| ALANGANALLUR |  | 12,509 |  | 15,657 |  |  |  | 19,596 |  |
| PALAMEDU |  | 9,564 |  | 11,386 |  |  |  | 13,555 |  |
| SINGAMPUNARI |  | 20,144 |  | 24,625 |  |  |  | 29,106 |  |
| SUB TOTAL B |  | 1,17,977 |  | 1,52,573 |  |  |  | 1,94,141 |  |
| 1430 RURAL HABITATIONS |  | 9,36,737 |  | 10,30,478 |  |  |  | 11,24,083 |  |
| ###### GRAND TOTAL |  | 12,14,583 |  | 13,93,516 |  |  |  | 15,92,399 |  |
| Requirement (in litres), at 135 lpcd for ULBs 90 lpcd for Melur & 70lpcd for A.Vellalapatty, Palamedu, Alanganallur, Singampuneri TPs 40 lpcd for Rural habitations (in mld) |  |  |  |  |  | 84.25 |  |  | 101.17 |
| Industrial Demand |  |  |  |  |  | 9.77 |  |  | 10.43 |
| TOTAL DEMAND |  |  |  |  |  | 94.02 |  |  | 111.60 |
| Existing Supply (in mld) |  |  |  | 38.74 |  | 38.74 |  |  | 38.74 |
| Net Requirement including 15% transmission loss (in mld) |  |  |  |  |  | 64.00 |  |  | 84.00 |
| Rate of supply at 23 hrs. pumping with minimum 10 lpm (in lpm) |  |  |  |  |  | 46,379 |  |  | 60,870 |
| Source | Collector well –3 nos with 16 Nos radial arms in 2 Tier in river Cauvery near Mettu mahathanapuram |  |  |  |  |  |  |  |  |
|  | Pumpset Turbine (100% stand bye) |  |  |  | 15500 lpm X 22 m (3+3) |  |  |  |  |
| Collection sump | 31.55 LL + 5.00 LL |  |  |  |  |  |  |  |  |
| Turbine Pumpset | 11,600 lpm x 92 m ( 4+2 Nos) (50% stand bye) |  |  |  |  |  |  |  |  |
| Pump room | 5m X 4m –3 Nos |  |  |  |  |  |  |  |  |
| Connecting main | 600 mm MS 6 mm – 8,800 m. |  |  |  |  |  |  |  |  |
| Booster station | Thogamalai |  | 31.55 LL+ 5.00 LL |  |  |  |  |  |  |
|  | Pannankombu |  | 31.55 LL+ 5.00 LL |  |  |  |  |  |  |
| Sump | Kottaiyur |  | 36.55 LL -1 No |  |  |  |  |  |  |
| Pumproom |  |  | 12m x 8 m (3 Nos) |  |  |  |  |  |  |
| Pumpset | Turbine Pumpset ( 4 Nos running parallel ) 50% stand bye |  |  |  |  |  |  |  |  |
|  |  |  | 11600 lpm X 74 m ( 4+2 Nos) |  |  |  |  |  |  |
|  |  |  | 11600 lpm X 93 m ( 4+2 Nos) |  |  |  |  |  |  |
| Intermediate/ Receiving sumps. | Capacity |  | Pumproom |  |  |  | Pumpset |  |  |
| A.Vellalapatty Rural | 6.80 LL |  |  |  |  |  |  |  |  |
| A.Vellalpatty TP | 1.80 LL |  | 5 m x 4 m |  |  |  | 166 lpm x 64 m |  |  |
|  |  |  |  |  |  |  | 250 lpm x 27 m |  |  |
| Madurai West | 2.40 LL |  | - |  |  |  | - |  |  |
| Alanganallur | 25.50 LL |  | 9 m x 5 m |  |  |  | 355 lpm x 45 m |  |  |
|  |  |  |  |  |  |  | 1,852 lpm x 105 m |  |  |
| Palamedu TP | 3.00 LL |  | 5 m x 4 m |  |  |  | 534 lpm x 21 m 58 lpm x 7m |  |  |
| Vadipatti Union | 1.05 LL |  | - |  |  |  | - |  |  |
| Guruvarpatti | 24.60 LL |  | 9 m x 5 m |  |  |  | - |  |  |
| Singampuneri TP | 9.70 LL |  | 5 m x 4 m |  |  |  | 2,198 lpm x 31 m |  |  |
| Melur MPTY | 40.00 LL |  | 8 m x 5 m |  |  |  | 334 lpm x 25 m |  |  |
| Mangulam (Madurai East) | 41.40 LL |  | 9 m x 5 m |  |  |  | 9,584 lpm x 42 m |  |  |
| Thirunagar TP | 3.20 LL |  | 8 m x 5 m |  |  |  | 925 lpm x 20 m |  |  |
| Paravai TP | 5.75 LL |  | 8 m x 5 m |  |  |  | 1,408 lpm x 33 m |  |  |
| Vilangudi TP | 7.15 LL |  | 8 m x 5 m |  |  |  | 1,775 lpm x 27 m |  |  |
| Thirumangalam MPTY | 14.90 LL |  | 8 m x 5 m |  |  |  | 326 lpm x 25 m |  |  |
|  |  |  |  |  |  |  | 819 lpm x 28 m |  |  |
|  |  |  |  |  |  |  | 2,288 lpm x 26 m |  |  |
| Athisivan Nagar | 3.00 LL |  | - |  |  |  | - |  |  |
| K.Meenakshipatti | 1.45 LL |  | - |  |  |  | - |  |  |
| Avaniapuram MPTY | 12.45LL |  | 8 m x 5 m |  |  |  | 1,581 lpm x 22 m |  |  |
|  |  |  |  |  |  |  | 1,319 lpm x 22 m |  |  |
| Panchayat & Inter mediate Sumps | 315 Nos. |  | -- |  |  |  |  |  |  |
| Transmission main & Feeder mains | 1100,900,800,700 mm MS pipes with thickness ranging from 8.8 mm to 7 mm. DI K7 & K9 –500 mm to 100mm |  |  |  |  |  | 369.69 km |  |  |
| Feeder mains to Rural beneficiaries | DI, PVC & GI Pipes –200 mm to 63 mm 4 ksc |  |  |  |  |  | 2154.26 Km |  |  |

| Name of Unions | Service Reservoirs (Rural Beneficiaries) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Distribution System (in Kms) |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 0.10 LL |  | 0.15 | 0.20 | 0.30 LL |  | 0.60 | 0.40 | 1.00 LL |  | 1.50 LL |  | 2.00 LL |  | Total |  |  |  |
|  | E | P | E | P | E | P | E | P | E | P | E | P | E | P | E | P | E | P |
| Melur | 77 | 12 | 9 | 6 | 133 | - | 28 | - | 4 | - | - | - | - | - | 251 | 18 | 326.30 | 10.50 |
| Kottam patty | 75 | 14 | - | 4 | 89 | - | 34 | 1 | 6 | - | - | - | - | - | 204 | 19 | 274.00 | 9.50 |
| Vadipatty | 19 | - |  | 1 | 35 | - | 15 | - | 6 | - | - | - | 2 | - | 77 | 1 | 125.50 | 0.80 |
| Alanga nallur | 35 | 1 |  |  | 60 | - | 42 | - | 10 | - | - | - | - | - | 147 | 1 | 242.50 | 0.50 |
| Madurai West | 44 | - | - | - | 60 | - | 50 | - | 23 | - | - | - | - | - | 177 | 0 | 306.00 | - |
| Madurai East | 89 | 13 | 5 | - | 95 | 1 | 51 | - | 12 | - | - | - | 1 | - | 253 | 14 | 358.00 | 8.10 |
| Thirup paran kundram | 57 | 6 | - | - | 91 | - | 37 | - | 10 | - | 1 | - | 4 | - | 200 | 6 | 306.50 | 4.50 |
| Thirumangalam | 37 | 2 | - | - | 82 | - | 29 | - | 2 | - | - | - | - | - | 150 | 2 | 220.00 | 2.0 |
| Total | 433 | 48 | 14 | 11 | 645 | 1 | 286 | 1 | 73 | - | 1 | - | 7 | - | 1,459 | 61 | 2,158.80 | 32.40 |

Dilapidated OHTs

| Sl. No. | Name of Union | Name of Panchayat | Name of Habitation | Capacity of SR proposed. |
| --- | --- | --- | --- | --- |
| 1. | Vadipatti | Thiruvedagam | Thiruvedagam | 60000 litres |
| 2. | Thirupparankundram | Chinthamani | Chinthamani | 60000 litres |
| 3. | Thirupparankundram | Vadivelkarlai | Vadivelkarai | 60000 litres |
| 4. | Kottampatti | Kunnarampatti | Kunnarampatti | 60000 litres |
| 5. | Melur | Soorakundu | Soorakundu | 60000 litres |
| 6. | Melur | Uranganpatti | Uranganpatti | 10000 litres |
| 7. | Melur | Uranganpatti | Pudupatti | 20000 litres |
| 8. | Melur | Uranganpatti | Ayyamuthanpatti | 20000 litres |
| 9. | Melur | Uranganpatti | Tharmachanapatti | 20000 litres. |

| Name of ULBs | Service Reservoirs (Urban Beneficiaries) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Distribution System (in Kms) |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 0.1 | 0.3 | 0.60 |  | 1.00 |  | 1.50 |  | 2.00 |  | 3.00 |  | 4.00 |  | 5.00 |  | 7.00 |  | 10.00 |  | Total |  |  |  |
|  | ( in Lakh Litres) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | E | E | E | P | E | P | E | P | E | P | E | P | E | P | E | P | E | P | E | P | E | P | E | P |
| Melur |  | - | - | - | - | - | - | - | - | - | 2 | - | - | - | 1 | - | 1 | - | - | - | 4 | - | 43.71 | - |
| Avania puram | - | - | - | - | - | - | - | - | - | - | 1 | - | 1 | - | - | - | - | - | 2 | - | 4 | - | 60.00 | 3.62 |
| Thiru manga lam | - | - | - | - | 1 | - | - | - | 1 | 2 | 2 | - | - | - | 1 | - | 1 | - | - | - | 6 | 2 | 51.60 | 12.86 |
| Paravai | - | - | 1 | - | 1 | - | - | - | 3 | 1 | 1 | - | - | - | - | - | - | - | - | - | 6 | 1 | 14.79 | 3.73 |
| Vilan gudi | - | - | 2 | - | 5 | 1 | 1 |  | 1 | 2 |  | - | - | - | - | - | - | - | - | - | 9 | 3 | 47.97 | 19.08 |
| Thiru nagar | - | - | - | - | - | 2 | - | - | 2 | - | 1 | - | - | - | - | - | - | - | - | - | 3 | 2 | 35.00 | 7.94 |
| A.Vellala patti | - | - | - | - | 2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | - | 8.50 | - |
| Alanga nallur | - | 1 | 3 | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | 5 | - | 17.00 | - |
| Pala medu | 4 | - |  | - |  | - |  | - | 2 | - |  | - |  | - |  | - |  | - |  | - | 6 | - | 14.10 | - |
| Singam puneri | - | - | 6 | - | 1 | - |  | - | - | - | 1 | - |  | - |  | - |  | - |  | - | 8 | - | 16.60 | - |
| Total | 4 | 1 | 12 | - | 10 | 3 | 1 | - | 10 | 6 | 8 | - | 1 | - | 2 | - | 2 | - | 2 | - | 53 | 8 | 309.27 | 39.19 |