## Sheet1 (hidden)
234799999999.99 | #VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!

## COVER
TAMIL NADU WATER SUPPLY AND DRAINAGE BOARD
COVER – II
PRICE BID
NAME OF WORK : Outsourcing of operation and Maintenance of under CWSS to 222 Habitation in Vedaranyam union, 114 Habitations in Muthupet union, Thiruvarur Municipality, Thiruthuraipoondi Municipality, Muthupet UTP,Vedaranyam Municipality, Thalainayar RTP and Bulk supply to 306 habitations in Thanjavur,Thiruvarur and Nagapattinam Districts for the period from 16.07.2022 to 31.03.2023

## Bill of QTY
NAME OF WORK : Outsourcing of operation and Maintenance of under CWSS to 222 Habitation in Vedaranyam union, 114 Habitations in Muthupet union, Thiruvarur Municipality, Thiruthuraipoondi Municipality, Muthupet UTP,Vedaranyam Municipality, Thalainayar RTP and Bulk supply to 306 habitations in Thanjavur,Thiruvarur and Nagapattinam Districts for the period from 16.07.2022 to 31.03.2023
BILL OF QUANTITIES
General
The Bill of Quantities shall contain items for the construction, installation, testing, commissioning and maintenance of the Works to be carried out by the Contractor
The Bill of Quantities will be used to calculate the Contract Price. The contractor shall be paid for the quantum of work done at the rate furnished for each item in the Bill of Quantities.
Where there is a discrepancy between the rates in words and figures, the lesser of the two will only be taken into consideration.
Where there is a discrepancy between the unit rate and line item total resulting from multiplying the unit rate by the quantity, the unit rate as quoted will govern.
Where there is an arithmetical discrepancy in the page total as well as grand total, the corrected total by the Employer will govern
The rates furnished in the BOQ shall be for carrying out the work in conformity to the BIS, TNBP and Technical Specifications and other Terms and Conditions set out in the Bid Document
All pages in the BOQ should be signed without omission. All corrections/over writing should be properly attested by the Bidder.
Change in the Quantities
If the final quantity of the work done differs from the quantity in the Bill of Quantities for the particular item/items, the rates as in the agreement for the relevant items shall be paid.
-----------------------------------------------------------------------------------------------------------------
Sl.No. Description of Quantity Specifi Unit Rate Amount
Item of Work cation ---------------------------
in in
Figures Words
-----------------------------------------------------------------------------------------------------------------

## General Abstract
GENERAL ABSTRACT.
NAME OF WORK: Outsourcing of operation and Maintenance of under CWSS to 222 Habitation in Vedaranyam union, 114 Habitations in Muthupet union, Thiruvarur Municipality, Thiruthuraipoondi Municipality, Muthupet UTP,Vedaranyam Municipality, Thalainayar RTP and Bulk supply to 306 habitations in Thanjavur,Thiruvarur and Nagapattinam Districts for the period from 16.07.2022 to 31.03.2023
Sl. No. | Schedule No | NAME OF COMPONENT | AMOUNT IN RUPEES.
1 | A1 | Operation and Maintenance of the Electro Mechanical installations, equipments,components, pipelines valves and appurtenances, water retaining structures | 0
2 | A2 | Repair works of the Electrical, Mechanical and Electro-mechanical item and leak & Burst | 0
|  | TOTAL | 0
#VALUE!
67972297
53215737.66
14756559.34

## A1
SCHEDULE - A1
NAME OF WORK : Outsourcing of operation and Maintenance of under CWSS to 222 Habitation in Vedaranyam union, 114 Habitations in Muthupet union, Thiruvarur Municipality, Thiruthuraipoondi Municipality, Muthupet UTP,Vedaranyam Municipality, Thalainayar RTP and Bulk supply to 306 habitations in Thanjavur,Thiruvarur and Nagapattinam Districts
Operation and Maintenance of the Electro Mechanical installations, equipments,components, pipelines valves and appurtenances, water retaining structures
S. No | Description of work | Quantity |  | Specifications | Unit | Rate |  | Amount
[6 empty] | in figures | in words.
1 | Operation and Maintenance of the Electro Mechanical installations, equipements, components,pipelines valves and appurtenances,water retaining structuress including protection of all scheme components from damages /theft undertaking legal actions for such untoward incidents,preventive maintenance, disinfection and deliverance of water as per quality standards and supply of earnmarked quantity of water to the beneficiaries as per stanndard operating procedures,Acts and rules in force and as directected by TWAD Board Oficers and excluding cost towards attending leak,burst repairs and replacement works to electro mechanical installations consumables for disinfection of water,cleaning of all water retaining structure. | 6850 | MLD | Special Specification | 1 MLD (One MLD) |  | #VALUE! | 0
| TOTAL -A1 | [6 empty] | 0

## THIRUPARKADAL (hidden)
SUPPLY, DELIVERY AND ERECTION OF CENTRIFUGAL MONOBLOC PUMPSET -CWSS TO 890 Rural habitations in Nagapattinam District.
UNION:THIRUMARUGAL | [5 empty] | Location: | THIRUPARKADAL
S.No. | Description | Qty |  | TNDSS&Specialspecification | Per | Rate |  | Amount (in Rupees)
[6 empty] | infigures | Inwords
1 | 2 | 3 |  | 4 | 5 | 6 | 7 | 8
1 | Supply and Delivery of cetrifugal monobloc pumpset capable of discharging the following 115 lpm against the foiiowing total head of 17m due to all causes (1 Set as Standbye) and suitable for installation in 5 m dia sump having depth of 5 m. | 2 | Sets |  | 1Set | 11246 | #VALUE! | 22492
The pumpset should conform to IS 9079/89.. The motor shall be suitable for operation in 3 phase 50 hetze 300/440 V AC supply. The motor winding will be suitable for D.O.L Starer. The insulation should be of class B type and suitable for operation on 3 phase 300/440 V 50 HZ Ac supply. The motor should conform to IS 7538. The pump should of compact horizontal shaft monobloc type without power transmission losses. The pump should be supplied with suitable size of CI friction less foot valve.with single rubber flab and ci strainer confirming to IS 10805
The pump should be manufactured with highgrade cast iron, casting with bronze impeller, Shaft steel, pump shaft with machanical seal and axuilary gland, speed of pump and motor should in the range of 2700 to 2900 RPM. The pump set should be supplied with suitable starter and panal board as specified below.
SPECIFICATION OF A 3 PHASE MOTOR CONTROL, PANEL BOARD SUITABLE FOR CETIFUGAL MONOBLOC PUMPSETS
1 | Supply and delivery of well mounting type control panel made from M. S. sheet 18 swg vermin proof box type with hinged front door and fixed sides with locking arragements suitable for errection in pumproom, complete with internal wiring, provision for cable fntry and twin earthing complete as per I.E. Rules. Two coats of grey colour enamel paint over one coat of red oxide primer shall be provided.The following accessories should be provided in the control panel.
a | One number three phase ISI standard miniature circuit breaker suitable for the motor (MDS, standard , SIEMENS, S&S Crompton Greaves makes) . It looks after the safety of the personal opening the Panel Board namely the on-off knob of the MCB should be projected outside the Panel Board.
b | Power capacitor Bank of ample capacity with ISI Mark. 2 KVAR .
c | One number 0-500 V.,65mm dia volt meter conforming to ISI 1254 with phase selector switch for all the ranges (MAKE IMF, AE, MICO & SHANTI)
d | One number 0-30 Amps, 65mm dia Ammeter, conforming to ISI 1254 with phase selector switch (Make : AE,IMP. MICO, SHANTHI) The Ammeter scale may be suitably graduated as required to record reading as per duty points .
e | One number DOL strater each with 3 Nos. overload relay and under voltage protection at current setting should have a range of 75% of FLC (make L&T culter-Hammer, Crompton Greaves, Siemens and GECALS and ABB)
f | One number voltage sensing single phasing preventor . The preventor must not trip upto 40 V line voltage unbalance but must trip between 2-10 seconds under single phasing with the rated, capacity motor connected with the panel - Make; Any reputed make.
g | One number 5 Amps 3 pin-socket with pin along with plug for flush mounted emergency lighting for all the ranges.
2 | Supply and Delivery of 1.1 KV grade 3.5 core 6 sq.mm PVC insulated steel armoured Aluminium conductor conform to IS 1554 Part I | 15 | Mts |  | 1 Mtr. | 70.5 | #VALUE! | 1057.5
3 | Laying the above cable inbetween the TNEB Supply point to the MV Panal Boards thorugh the Change Over Switch | 15 | Mts |  | 1 Mtr. | 25 | #VALUE! | 375
4 | Jointing the above cable between the TNEB Supply Point, Change Over Switch and the MV Panal Boards. | 6 | Joints |  | 1 Jt. | 70.5 | #VALUE! | 423
5 | Supply and delivery of 1.1 KV grade 3 core 4 Sq. mm. PVC insulated steel armoured Aluminium conductor conform to IS 1554 part I for the motor of 115 lpm x 17 m pumpset | 2 x = | 10 20 Mts |  | 1 Mtr. | 54.1 | #VALUE! | #VALUE!
6 | Laying the above cable between the MV Panel Boards out going control MCBs to the motors through Starters. | 20 | Mts |  | 1 Mtr. | 25 | #VALUE! | 500
7 | Jointing the above cable between theMVPanel boards out going control MCBs to the motors mentioned in Sl. NO. 1. Through the starters. | 4 | Joints |  | 1Jt. | 54.1 | #VALUE! | 216.4
8 | Supply, delivery and fixing of Wall Mounting type 32 Amps TPN Change over switch | 1 | No. |  | 1 No. | 850 | #VALUE! | 850
9 | Providing pump house lighting as per IE rules using PVC conduit pipes and PVC insulated wire with control switches circuit fuses including PVC insulated two core 2.5 Sq.mm. Copper wire cable and 1 run of 12 SWG Gi wire for earhing with required number of chokes switches, 5 amps plug point and sockets etc., complete suitable for pumphouse wiring with the following 1 No. 16 Amps TPN switch to control lighting circuit, 2nos. of 40 W box type 1200 mm long flouerscent tube light fittings with choke and starter to be fixed inside the pumproom, 1 no, of 250 W Sodium Vapour light fitting with lamp & with suitable GI wall brackets and clamps to fix on the top of the front side outside of the pumproom,1no. 100 w bulkhead water proof light fitting set to be fixed on the other side (outside-Back) of the pump house. | 1 | Set |  | 1 Set. | 3481 | #VALUE! | 3481
10 | Twin copper earthing arrangements for all the plants and equipments in the pumphouse as per rules including construction of masonry pit with RCC slab | 1 | Set |  | 1Set | 5000 | #VALUE! | 5000
11 | Supply and delivery of bulk type interchangeable direct reading water meter conform to IS 2273 to measure the flow with removable machanism suitable to install in the pumping main of following size 140mm PVC Pipe. | 1 | NO. |  | 1 No. | 35200 | #VALUE! | 35200
12 | Erection, testing and comminsioning of the pumping plants and the electrical accessories including meter and gauges etc., as per IE rules and also including laying jointing of pipes and specials and valves with jointing materials, construction of CC bed for pumpset and for supporting the pipes. | 2 | Sets |  | 1 Set | 2008 | #VALUE! | 4016
13 | Supply delivery of 150mm dia pressure gauge 10 Kg /cm2 for suction and delivery of Centrifugal pumpsets with Red marking G.M coke and Copper impulse tube etc., to be fixed on teek wood board to be mounted on the wall of the pump house | 4 | sets |  | 1Set | 1500 | #VALUE! | 6000
14 | Supply and delivery of the following Pipes and Specials
a | 50mm G.I. Medium pipes for the erection of pumpset.(for suction pipe) | 12 | Mtre |  | 1 Mtr. | 153 | #VALUE! | 1836
b | 50mm G.I. Bend | 2 | Nos. |  | Each | 101.5 | #VALUE! | 203
c | 40mm G.I. Medium pipes (Delivery) | 12 | Mtre |  | 1 Mtr. | 109 | #VALUE! | 1308
d. | 40mm G.I. Bend | 2 | Nos |  | Each | 68.97 | #VALUE! | 137.94
e | 40mm G,M, Gate Valve with ISI marks. | 2 | Nos |  | Each | 705 | #VALUE! | 1410
f | 40mm. G.M. Non Return. valve with ISI marks. | 2 | Nos |  | Each | 500 | #VALUE! | 1000
g | 50mm G.I. Flange Set | 3 | Sets |  | 1 Set | 33 | #VALUE! | 99
h | 40mm G.I. Flange Set | 2 | No |  | Each | 25 | #VALUE! | 50
I | 125 mmx40mm GI R educer | 1 | No. |  | Each | 222 | #VALUE! | 222
j | 40 mm GI Nipple | 1 | No |  | Each | 34.2 | #VALUE! | 34.2
k | 40m G.I TEE | 1 | No |  | Each | 61.45 | #VALUE! | 61.45
l | 40mm G.I Union | 1 | Nos |  | Each | 90.15 | #VALUE! | 90.15
m | 140mm PVC Threaded coupler | 1 | No |  | Each | 101.3 | #VALUE! | 101.3
15 | Supply of mannuals giving details description of all the equipments mentioned above with address of the dealer and manufactures operation system and maintainance schedule etc., | 2 | Set
16 | Suply delivery and fixing of a teek wood board ( BOx type ) 18" x18" x2.5 " with 4 nos of suitable fuse carrier and 32 Amps TPN switch to be fixed on the wall rigidly with clamps bolts and nuts to receive supply from T.N.E.B and to control incoming supply | 1 | Set |  | 1Set | 1010 | #VALUE! | 1010
17 | Obtaining power supply including cost of following materilals and eneaging B licence holder.EB fee for Application form and deposit amount will be borne by the board | 1 | Set |  | 1Set | 5000 | #VALUE! | 5000
| 1. Aerial fuse board with suitable aerial fuse carrier ( 3 Nos) | [5 empty] | #VALUE! | 0
| 2. Wall mounting type MS cubical E.B. meter box with fuse carriers ( 3 Nos ) of suitable capacity at E.B supply point. This box is also to accommodate T.N.E.B. energy meter with proper ventilation as approved by T.N.E.B. | [5 empty] | #VALUE! | 0
| 3. Supply and laying of suitable size PVC insulated copper conductor wire from Aerial fuse to E.B. Supply point including cost of G.I wires,reels 25 mm pipes, G.I. Specials , inserting G.I pipes in wall, cement patch up etc complete as per I.E rules. | [5 empty] | #VALUE! | 0
18 | Supply and delivery of Following set of Tools and plants | 1 | Set |  | 1Set | 3690 | #VALUE! | 3690
| 1. 6" Chain Wrench Best Indian make - 1 No. | [5 empty] | #VALUE! | 0
| 2. 200 mm Screw driver 825 Taparia Make - 1 No. | [5 empty] | #VALUE! | 0
| 3. 300 mm Screw driver 829 Taparia Make - 1 No. | [5 empty] | #VALUE! | 0
| 4. Lever Type Grease gun - 1 No. | [5 empty] | #VALUE! | 0
| 5. Hacksaw frame with blade - 1 No. | [5 empty] | #VALUE! | 0
| 6. DE spanner set 6 to 32 Jhalani Make - 1 set | [5 empty] | #VALUE! | 0
| 7. Ring spanner set 6 to 32 Jhalani Make - 1 set | [5 empty] | #VALUE! | 0
| 8. Pipe Wrench 24 " Jhalani Make - 1 set | [5 empty] | #VALUE! | 0
| 9. Pipe Wrench 14 " Jhalani Make - 1 set | [5 empty] | #VALUE! | 0
19 | Supply and delivery of Safety appliances consisting of 8 Nos of electrical quality 1 m x 1m x 6mm thick rubber mat , to be laid in front of the panel board and motors of centrifugal , monoblock pumpsets, one pair of hand gloves tested for 11/22 KV with wooden box tested with french chalk powder and one no of Laminated shock treatment chart. 1 No. of 2 Kg capacity dry chemical powder type fire extinguisher | 1 | SET |  | 1Set | 2920 | #VALUE! | 2920
| Total | [6 empty] | #VALUE!
Free of cost

## A2
SCHEDULE - A2
NAME OF WORK : Outsourcing of operation and Maintenance of under CWSS to 222 Habitation in Vedaranyam union, 114 Habitations in Muthupet union, Thiruvarur Municipality, Thiruthuraipoondi Municipality, Muthupet UTP,Vedaranyam Municipality, Thalainayar RTP and Bulk supply to 306 habitations in Thanjavur,Thiruvarur and Nagapattinam Districts
Repair works of the Electrical, Mechanical and Electro-mechanical item and leak & Burst
S. No | Description of work | Quantity |  | Specifications | Unit | Rate |  | Amount
[6 empty] | in figures | in words.
1 | Attending Leaks in the pipelines of this CWSS for the following items as per the standard procedure including earthwork excavation, dewatering, removing, relaying,jointing,civil works,cost of materials and all other incidental charges etc complete with in the stipulated time limit as specified in clause 2.6.4 of General conditions of Contact-Part II.(The specifications for attending leaks has to be detailed based on the data prepared and rate approval obtained for each size and material of pipes.The specification has to be mentioned under the clause 1.7 of GCC-Part-I) |  |  | Special Specification |  |  | #VALUE! | 0
a | 63mm 4 ksc PVC Pipes | 13 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
b | 75mm 4 ksc PVC Pipes | 10 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
c | 90mm 4 ksc PVC Pipes | 10 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
d | 110mm 4 ksc PVC Pipes | 4 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
e | 140mm 4 ksc PVC Pipes | 1 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
f | 160mm 4 ksc PVC Pipes | 1 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
g | 350mm PSC pipe using cement joint | 1 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
h | 400mm PSC pipe using cement joint | 1 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
i | 450mm PSC pipe using cement joint | 1 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
j | 600mm PSC pipe using cement joint | 6 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
k | 700mm PSC pipe using cement joint | 1 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
l | 800mm PSC pipe using cement joint | 1 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
m | 900mm PSC pipe using cement joint | 11 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
n | 1100mm PSC pipe using cement joint | 17 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
o | 600mm PSC pipe using Plain collar | 6 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
p | 900mm PSC pipe using Plain collar | 2 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
q | 1100mm PSC pipe using Plain collar | 2 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
r | 600mm PSC pipe using step collar | 1 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
s | 900mm PSC pipe using step collar | 3 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
t | 1100mm PSC pipe using step collar | 5 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
u | 350 mm MS pipe by welding | 1 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
v | 400 mm MS pipe by welding | 1 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
w | 450 mm MS pipe by welding | 1 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
x | 600 mm MS pipe by welding | 3 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
y | 800 mm MS pipe by welding | 1 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
z | 900 mm MS pipe by welding | 6 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
aa | 1100 mm MS pipe by welding | 10 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
ab | Earthwork excavation for attenting MS welding portion | 84 | cum |  | 1 Cum (One Cubic Metre) |  | #VALUE! | 0
ac | Refilling for excavated earth in MS welding portion | 84 | cum |  | 1 Cum (One Cubic Metre) |  | #VALUE! | 0
ad | Dewatering of MS welding | 188.05 | Hrs |  |  |  | #VALUE! | 0
2 | Rewinding of motors in pumping station in the Electrical, Mechanical and Electro-mechanical items to bring back the scheme / components into normal running conditition as per standard specification including all labour charges, cost of materials and all incidental charges within the stipulated time limit etc., complete as specified in Clause 2.8 of General conditions of Contract Part II etc as directed by TWAD Board officers |  |  | Special Specification |  |  | #VALUE! | 0
a | Repairing and reconditioning of Pump for 6HP Submersible Pumpset-Sump at Manikaraiyur,Keelamanchery,Pattavarthy,Koonanchery,AnnaNagar,Nallur,Nallur BP tank,Govindakudi,Chandrasekarapuram,Semmangudi,Kottaiyur,Poovanur,Kadambur,Rajappansavadi,Kuruvaimozhi,Vanjur,Karuvakulam,Needamangalam | 2 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
b | Repairing and reconditioning of Pump for 150 HP V.T Pumpset including all material,labour,etc at Thiruvarur BS ,Thiruthuraipoondi, | 1 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
c | Repairing and reconditioning of Pump for 20 HP HSC Pumpset including all material,labour,etc at Thiruvarur BS ,Thiruthuraipoondi, | 2 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
d | Repairing and reconditioning of Pump for 90 HP HSC Pumpset including all material,labour,etc at Vanduvanchery | 1 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
e | Repairing and reconditioning of Pump for 60 HP HSC Pumpset including all material,labour,etc at Vanduvanchery | 1 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
f | Repairing and reconditioning of Pump for 45 HP HSC Pumpset including all material,labour,etc at Vanduvanchery | 1 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
g | Repairing and reconditioning of Pump for 25 HP HSC Pumpset including all material,labour,etc at Thiruvarur BS | 1 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
h | Repairing and reconditioning of Pump for 35 HP HSC Pumpset including all material,labour,etc at Thiruthuraipoondi B.S | 1 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
i | Repairing and reconditioning of Pump for 7.5HP Submersible Pumpset-Sump at Thiruthuraipoondi B.S | 1 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
j | Repairing and reconditioning of Pump for 2 HP HSC Pumpset including all material,labour,etc at Mannikarai, Annanagar, Chanrasekarapuram, Semmangudi, Alangudi (4nos),Kottaiyur,Poovanur, Rajapaiyanchavadi, Kuruvaimozhi, Vanjiyur, Karuvakulam, MAZHAVARAYANALLUR,Adhichapuram,Thirukalar,Thirupathur,(4 nos)Vilakkudi (4 nos) Kadiyachery, Thenkasi, Madapuram,Nedum balam(4nos)Pamani (6 nos), | 3 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
k | Repairing and reconditioning of Pump for 3 HP HSC Pumpset including all material,labour,etc at Keelamanchery,Pattavarthy,Manavalanpettai, Nallur, Kadambur,Rajapaiyanchavadi,Vilakkudi, Kadiyachery, Madapuram, Kattimadu(4 nos), | 8 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
l | Repairing and reconditioning of Pump for 5 HP HSC Pumpset including all material,labour,etc at Koonanchery, Thiyasamudram,Govindangudi, Semmangudy, Alangudy, Kottaiyur,Kottur, Meenambanallur, Kadiyachery, Korkkai | 7 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
m | Repairing and reconditioning of Pump for 2 to 5 HP HSC Pumpset including all material,labour,etc at Muthupettai block | 31 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
n | Repairing and reconditioning of Pump for 2 to 5 HP HSC Pumpset including all material,labour,etc at Vedaranyam block | 9 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
o | Repairing and reconditioning of Pump for 12.5 HP HSC Pumpset including all material,labour,etc at Vedaranyam Sump | 1 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
p | Replacement of Starter 2HP | 1 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
q | Replacement of Starter 3 HP | 2 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
r | Replacement of Starter 5 HP | 1 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
s | Supply and delivery of the following Electrical works:consumable items at the site of work carry out the general maintenance works |  | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
t | Volt meter SR 96 600 V-AC | 2 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
u | Ammeter SR 96 5D/5A C.T.operated-AC | 2 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
v | LED Outdoor fittings a)30 W LED street light fittings | 3 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
w | Power capacitor for power factor improvement with oil filled with discharge resistance 3 phase 415/440V 50 HZ conforming to ISS:2834 with ISI marking | 240 | KVAR |  | 1 kvar. (One KVAR) |  | #VALUE! | 0
x | Supply and delivery of Transformer oil at Thiruvaikavur and Vanduvanchery | 600 | Lts |  | 1 Ltr. (One Litre) |  | #VALUE! | 0
y | Replacement of 50 mm GI pipe damaged during road wideninig works | 50 | M |  | 1 M (One Metre) |  | #VALUE! | 0
z | Replacement of 65 mm GI pipe damaged during road wideninig works | 30 | M |  | 1 M (One Metre) |  | #VALUE! | 0
aa | Replacement of 80 mm GI pipe damaged during road wideninig works | 60 | M |  | 1 M (One Metre) |  | #VALUE! | 0
ab | Replacement of 100 mm GI pipe damaged during road wideninig works | 18 | M |  | 1 M (One Metre) |  | #VALUE! | 0
3 | Replacement of Underground Utilities (GI Pipe) damaged during earthwork excavations for pipe laying works including cost of additional earthwork excavation in all soil strata, including BT/CC road cutting, removal of slushy soil and replacing the pipeline with sound pipe, including supply and delivery of GI pipes, coupler, Union, jointing materials and required specials, cutting, threading, conveying , laying, jointing and cost of refilling for the additional earthwork etc complete and as directed by the TWAD board officers. |  |  | Special Specification |  |  | #VALUE! | 0
a | 50mm Dia GI Pipe | 18 | M |  | 1 M (One Metre) |  | #VALUE! | 0
b | 65mm Dia GI Pipe | 15 | M |  | 1 M (One Metre) |  | #VALUE! | 0
c | 80mm Dia GI Pipe | 18 | M |  | 1 M (One Metre) |  | #VALUE! | 0
d | Earthwork excavation for attenting culvert crossing works due to road widening | 70 | cum |  | 1 Cum (One Cubic Metre) |  | #VALUE! | 0
e | Refilling for excavated earth in culvert crossing works due to road widening | 190 | cum |  | 1 Cum (One Cubic Metre) |  | #VALUE! | 0
4 | supply and delivery of G.I.specials |  |  | Special Specification |  |  | #VALUE! | 0
a | 50mm GI Elbow | 24 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
b | 65mm GI Elbow | 24 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
c | 80mm GI Elbow | 36 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
d | 100mm GI Elbow | 36 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
e | 125mm GI Elbow | 42 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
5 | Supply and delivery of pvc threaded adopter | [5 empty] | #VALUE! | 0
a | 63mm pvc | 12 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
b | 75mm pvc | 12 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
c | 90mm pvc | 18 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
d | 110mm pvc | 18 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
e | 140mm pvc | 21 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
6 | Supply and deliveryof DI Single Chamber air release valve |  |  | Special Specification |  |  | #VALUE! | 0
a | 200 mm | 8 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
7 | Supply and deliveryof G.M Gate valve | [5 empty] | #VALUE! | 0
a | 50mm | 4 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
b | 65 mm | 2 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
c | 80 mm | 3 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
d | 100mm | 2 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
e | 125mm | 2 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
8 | Cleaning of all storage points like sumps, stand posts of various capacities available in this scheme at a frequency of once in two months including scrapping the inner side of compartment completely, dewatering, desilting using rquired machineries , materials , labour, all incidental chargs , application of bleaching powder/ solution etc complete and as directed by TWAD Board officers |  |  | Special Specification |  |  | #VALUE! | 0
a | 5000 Liters Capacity sump @ Vedaranyam Union | 4 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
b | 10000 Liters Capacity sump @ Vedaranyam Union | 7 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
c | 30000 Liters Capacity sump @ Vedaranyam Union,Thiruthuraipoondi,Mannargudi,Muthupetai&Papanasam Union 46x3 Times | 34.5 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
d | 50000 Liters Capacity sump @ Vedaranyam Union | 1 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
e | 55000 Liters Capacity sump @ Needamangalam Union | 1 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
f | 60000 Liters Capacity sump @ Papanasam Union,Mannargudi,Thiruthuraipoondi union,Vedaranyam Union | 4 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
g | 70000 Liters Capacity sump @ Muthupettai Union 11 | 11 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
h | 1.00 LL Liters Capacity sump @ Papanasam,Valangaiman,Kottur,Needamangalam,Mannargudi,Thiruthuraipoondi Union | 11 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
i | 1.2 LL Liters Capacity sump @ Muthupettai Union | 1 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
j | 1.5 LL Liters Capacity sump @ Papanasam,Valangaiman,Kottur,Needamangalam,Thiruthuraipoondi ,Kumbakonam ,Muthupettai Union | 3 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
k | 2.00 LL Liters Capacity sump @ Papanasam,Kottur,Thiruthuraipoondi Union | 3 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
l | 2.5 LL Liters Capacity sump @ Valangaiman,Thiruthuraipoondi Union | 3 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
m | 3.00 LL Liters Capacity sump @ Thiruthuraipoondi | 1 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
n | 3.5 LL Liters Capacity sump @ Muthupettai Union | 3 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
o | 11.00 LL Liters Capacity sump @ Thiruvaikavur,Thiruvarur,Edaiyur Sanganthi,Vanduvanchery. | 3 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
| Total - A | [5 empty] | #VALUE! | 0
B | PUTHAGARAM CWSS | [5 empty] | #VALUE! | 0
1 | Attending Leaks in the pipelines of this CWSS for the following items as per the standard procedure including earthwork excavation,dewatering,removing,relaying,jointing,civil works,cost of materials and all other incidental charges etc complete with in the stipulated time limit as specified in clause 2.6.4 of General conditions of Contact-Part II.(The specifications for attending leaks has to be detailed based on the data prepared and rate approval obtained for each size and material of pipes.The specification has to be mentioned under the clause 1.7 of GCC-Part-I) |  |  | Special Specification |  |  | #VALUE! | 0
a | 63mm 4 ksc PVC Pipes | 8 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
b | 75mm 4 ksc PVC Pipes | 2 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
c | 90mm 4 ksc PVC Pipes | 6 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
d | 110mm 4 ksc PVC Pipes | 10 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
e | 140mm 4 ksc PVC Pipes | 18 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
2 | Rewinding of motors in pumping station in the Electrical, Mechanical and Electro-mechanical items to bring back the scheme / components into normal running conditition as per standard specification including all labour charges, cost of materials and all incidental charges within the stipulated time limit etc., complete as specified in Clause 2.8 of General conditions of Contract Part II etc as directed by TWAD Board officers |  |  | Special Specification |  |  | #VALUE! | 0
a | Repairing and reconditioning of Pump for 5 HP HSC Pumpset including all material,labour,etc at NOCHIYUR | 2 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
b | supply and delivery of G.I.specials | [5 empty] | #VALUE! | 0
c | 50mm GI Elbow | 4 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
d | 65mm GI Elbow | 4 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
e | 80mm GI Elbow | 8 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
f | 100mm GI Elbow | 8 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
g | 125mm GI Elbow | 12 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
3 | Supply and delivery of pvc threaded adopter | [5 empty] | #VALUE! | 0
a | 63mm pvc | 2 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
b | 75mm pvc | 2 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
c | 90mm pvc | 4 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
d | 110mm pvc | 4 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
e | 140mm pvc | 6 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
f | Earthwork excavation for attenting culvert crossing works due to road widening | 24 | cum |  | 1 Cum (One Cubic Metre) |  | #VALUE! | 0
g | Refilling for excavated earth in culvert crossing works due to road widening | 24 | cum |  | 1 Cum (One Cubic Metre) |  | #VALUE! | 0
h | 1.00 LL Liters Capacity sump @ Nochiyur in Kottur Union 1x3 Times | 3 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
| Total - B | [5 empty] | #VALUE! | 0
C | THIRUVASALADI CWSS | [5 empty] | #VALUE!
1 | Attending Leaks in the pipelines of this CWSS for the following items as per the standard procedure including earthwork excavation,dewatering,removing,relaying,jointing,civil works,cost of materials and all other incidental charges etc complete with in the stipulated time limit as specified in clause 2.6.4 of General conditions of Contact-Part II.(The specifications for attending leaks has to be detailed based on the data prepared and rate approval obtained for each size and material of pipes.The specification has to be mentioned under the clause 1.7 of GCC-Part-I) |  |  | Special Specification |  |  | #VALUE! | 0
a | 63mm 4 ksc PVC Pipes | 1 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
b | 75mm 4 ksc PVC Pipes | 1 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
c | 90mm 4 ksc PVC Pipes | 2 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
d | 110mm 4 ksc PVC Pipes | 1 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
e | 140mm 4 ksc PVC Pipes | 1 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
2 | Rewinding of motors in pumping station in the Electrical, Mechanical and Electro-mechanical items to bring back the scheme / components into normal running conditition as per standard specification including all labour charges, cost of materials and all incidental charges within the stipulated time limit etc., complete as specified in Clause 2.8 of General conditions of Contract Part II etc as directed by TWAD Board officers |  |  | Special Specification |  |  | #VALUE! | 0
a | Repairing and reconditioning of Pump for 7.5HP Submersible Pumpset- | 1 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
b | Replacement of 50 mm GI pipe damaged during road wideninig works | 6 | M |  | 1 M (One Metre) |  | #VALUE! | 0
c | Replacement of 65 mm GI pipe damaged during road wideninig works | 6 | M |  | 1 M (One Metre) |  | #VALUE! | 0
d | Replacement of 80 mm GI pipe damaged during road wideninig works | 6 | M |  | 1 M (One Metre) |  | #VALUE! | 0
e | Replacement of 100 mm GI pipe damaged during road wideninig works | 7 | M |  | 1 M (One Metre) |  | #VALUE! | 0
3 | Supply and delivery of G.I.specials | [5 empty] | #VALUE! | 0
a | 50mm GI Elbow | 4 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
b | 65mm GI Elbow | 4 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
c | 80mm GI Elbow | 8 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
d | 100mm GI Elbow | 8 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
e | 125mm GI Elbow | 8 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
4 | Supply and delivery of pvc threaded adopter | [5 empty] | #VALUE! | 0
a | 63mm pvc | 2 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
b | 75mm pvc | 2 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
c | 90mm pvc | 4 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
d | 110mm pvc | 4 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
e | 140mm pvc | 6 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
| Total - C | [5 empty] | #VALUE! | 0
D | BOOTHAMANGALAM CWSS | [5 empty] | #VALUE! | 0
1 | Attending Leaks in the pipelines of this CWSS for the following items as per the standard procedure including earthwork excavation,dewatering,removing,relaying,jointing,civil works,cost of materials and all other incidental charges etc complete with in the stipulated time limit as specified in clause 2.6.4 of General conditions of Contact-Part II.(The specifications for attending leaks has to be detailed based on the data prepared and rate approval obtained for each size and material of pipes.The specification has to be mentioned under the clause 1.7 of GCC-Part-I) |  |  | Special Specification |  |  | #VALUE! | 0
a | 63mm 4 ksc PVC Pipes | 2 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
b | 75mm 4 ksc PVC Pipes | 1 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
c | 90mm 4 ksc PVC Pipes | 2 | Nos. |  | 1 No. (One Number) |  | #VALUE! | 0
| Total - D | [6 empty] | 0
| GRAMD TOTAL (A+B+C+D) - 2 | [6 empty] | 0