## Vedaranyam (2)
SALIENT DETAILS
CWSS TO VEDARANYAM
1 | Scheme Cost
a) | Installation cost | Rs.133.05 Crores
b) | Annual Maintenance cost | Rs.347.55 lakhs
2 | Administrative approval No&Amount | GO Ms No.11/MAWS/dt:28.1.2000 for RS.133.05 Crores
3 | Technical sanction No & Amont | CE/ER/TNJ/ No.55/99-2000 dt:3.2.200 for Rs.133.05 Crores
4 | Beneficiaries
THANJAVUR DISTRICT
56 Rural habitation in Kumbakonam and Papanasam union.
THIRUVARUR DISTRICT
Thiruvarur MPTY, Muthupet TP, 364 Rural habitation in Valangaiman,Needamangalam,Mannargudi,Kottur, Thiruthuraipoondi and Muthupet union.
NAGAPATTINAM DISTRICT
Vedaranyam MPTY,Thalainayur TP, 222 Rural habitation in Vedaranyam union.
5 | Populations
a) | Intermediate(Year) | 652318 (2011)
b) | Ultimate (Year) | 816500 (2026)
6 | Level of service | 90 lpcd, 70 lpcd for TPs and 40 lpcd for Rural Habs.
7 | Designed Quanity
a) | Present (Year) | 31.193 MLD - (2008)
b) | Intermediate (year) | 35.31 MLD - (2011)
c) | Ultimate (Year) | 43.59 MLD - (2026)
8 | Year of completion and Commissioning | 2004 | 0.87521
a) | Original Scheme | Original Scheme | 0.84033
b) | Improvement Scheme | _____ | 0.82051
9 | Head works with Source details | Collector well 2 Nos in River coleroon (Edaikudi and Thiruvaikkavur) | 1.2921
10 | Pumpset
a) | Type | Vertical Turbine Pumpset.
b) | Duty | 14365 lpm X18m(80HP)- 1 No. each in Collector wells
c) | Common sump at Thiruvaikavur. | 11.00 Lakh litres capacity.
14365 lpm X 35m(150 HP)-8m dia common sump.
2 Nos.of totally 300 HP runing in parallal
11 | Hours of Pumping | 20 Hrs.
a) | Pumping main
b) | From Head work to Nallur BPT
c) | 900 mm PSC main laid in the centre of road - Soil made up of sandy and sugar cane carriying roads = 8790 m
d) | Nallur BPT = 5.00 Lakh litres capacity
12 | Gravity main
a) | From Nallur BPT to Needamangalam BPT
b) | 1100 mm PSC main laid in the centre of state high ways road - Soil made up of sandy and river bund portion and Agri. Lands. = 25710 m
c) | Needamangalam BPT = 5.00 Lakh litres capacity.
13) | Gravity main
a) | From Needamangalam BPT to Thirupathur Tee point
b) | 1100 mm PSC main laid in the state high ways road and Clay Soil and river bund portion.=31500 m
14 | Gravity main
From Kottaiyur Branch point to Thiruvarur Municipality - 600 mm PSC main = 23160 m
Thiruvarur Booster sump - 11.00 Lakh litres capacity
| Pumpsets | 20.00 HP HSC pumpset duty 2840 Lpm X 21 m head.
25.00 HP HSC pumpset duty 2410 Lpm X 27 m head.
Gravity main
Thirupathur Tee point to Thiruthurai poondi booster
600 mm PSC main laid in the state high ways road and Clay Soil and river bund portion.=12000 m
Gravity main
Thirupathur Tee point to Edaiyur Sanganthi booster
900 mm PSC main laid in the centre of state high ways road - Soil made up of sandy and river bund portion and Agri. Lands.=15980 m
Gravity main
Edaiyur Sanganthi to Vanduvan cheri booster
| 800 mm PSC main laid in the state high ways road edge and river bund portion with PCB (problem)=13695 m |  | 15.65
Thiruthuraipoondi Booster - 3.00 Lakh litres capacity
| Pumpsets | 20.00 HP HSC pumpset duty 2700 Lpm X 20 m head.
35.00 HP HSC pumpset duty 2719 Lpm X 35 m head.
Pumping main
Thiruthuraipoondi to Thainayuru= 19110 m
350 mm PSC main laid in ECR road - Soil made up of clay and Agri. Lands =19110 m
Thiruthuraipoondi to Melamaruthur
140 mm PVC to 63 mm PVC
Edaiyur Sanganthi Booster - 11.00 Lakh litres capacity
| Pumpsets | 60.00 HP HSC pumpset duty 4200 Lpm X 44 m head.
20.00 HP HSC pumpset duty 1664 Lpm X 20 m head.
Pumping main
Edaiyur Sanganthi to Muthupettai UTP= 15450 m
350 mm PSC main laid in ECR road - Soil made up of clay and Agri. Lands =26000 m
Pumping main
Edaiyur Sanganthi to Thondiakadu= 9500 m
350 mm PSC main laid in state highway road - Soil made up of clay and Agri. Lands =9500 m
Vanduvancheri Booster - 11.00 Lakh litres capacity
| Pumpsets | 90.00 HP HSC pumpset duty 5010 Lpm X 52 m head.
60.00 HP HSC pumpset duty 4225 Lpm X 45 m head.
45.00 HP HSC pumpset duty 4000 Lpm X 34 m head.
Pumping main
Vanduvan cheri booster to Vedaranyam Mpty
450 mm PSC main laid in the centre of state high ways road - Soil made up of sandy and river bund portion and Agri. Lands =25675 m
Pumping main
Vanduvan cheri booster to Kodiakarai = 26000 m
350 mm PSC main laid in the centre of state high ways road - Soil made up of sandy and river bund portion and Agri. Lands =26000 m
Pumping main
Vanduvan cheri booster to Pushpavanam = 31025 m
450 mm-350 mm PSC main laid in the centre of state high ways road - Soil made up of sandy and river bund portion and Agri. Lands =26000 m
14 | Feeder Main | 438 Kms
15 | No of Group sump with capacity | 104 sumps(10,000 litres to 2.50 lakhs litres.)
16 | Service Reservoirs with capacity | 397 (10000 litres to 1.00 LL )
17 | Separate power feeder main details | Provided at Headworks at Thiruvaikkavur. Booster stations at Thiruvarur, Edayur sanganthi,Thiruthuraipoondi, and Vanduvancheri
18 | Distribution system | 655 Km.

## Vedaranyam
SALIENT DETAILS
CWSS TO VEDARANYAM
1 | Scheme Cost
a) | Installation cost | Rs.133.05 Crores
b) | Annual Maintenance cost | Rs.347.55 lakhs
2 | Administrative approval No&Amount | GO Ms No.11/MAWS/dt:28.1.2000 for RS.133.05 Crores
3 | Technical sanction No & Amont | CE/ER/TNJ/ No.55/99-2000 dt:3.2.200 for Rs.133.05 Crores
4 | Beneficiaries
THANJAVUR DISTRICT
56 Rural habitation in Kumbakonam and Papanasam union.
THIRUVARUR DISTRICT
Thiruvarur MPTY Muthupet UTP 364 Rural habitation inValangaiman,Needamangalam,Mannargudi,Kottur, Thiruthuraipoondi and Muthupet union.
NAGAPATTINAM DISTRICT
Vedaranyam MPTY,Thalainayur RTP,222 Rural habitation in Vedaranyam union.
5 | Populations
a) | Intermediate(Year) | 652318 (2011)
b) | Ultimate (Year) | 816500 (2026)
6 | Level of service | 90 lpcd, 70lpcd for TPs and 40lpcd for Rural Habs.
7 | Designed Quanity
a) | Present (Year) | 31.193 MLD - (2008)
b) | Intermediate (year) | 35.31 MLD - (2011)
c) | Ultimate (Year) | 43.59 MLD - (2026)
8 | Year of completion and Commissioning | 2004 | 0.87521
a) | Original Scheme | Original Scheme | 0.84033
b) | Improvement Scheme |  | 0.82051
9 | Head works with Source details | Collector well 2 Nos in River coleroon (Edaikudi and Thiruvaikkavur) | 1.2921
10 | Pumpset
a) | Type | Vertical Turbine Pumpset.
b) | Duty | 14365 lpm X18m(80HP)- 4 Nos.( each -2 Nos. in Collector wells )
c) | Common sump at Thiruvaikavur. | 11.00 Lakh litres capacity.
14365 lpm X 35m(150 HP)-8m dia common sump.
3 Nos.of totally 300 HP runing in parallal ( 1 No. Stand bye)
11 | Hours of Pumping | 20 Hrs.
a) | Pumping main
b) | From Head work to Nallur BPT
c) | 900 mm PSC main laid in the centre of road - pipe line laid in sandy and clayey soil = 8790 m |  | 181.9
d) | Nallur BPT = 5.00 Lakh litres capacity
12 | Gravity main
a) | From Nallur BPT to Needamangalam BPT
b) | 1100 mm PSC main laid in the centre of state high ways road - pipe line laid in sandy and clayey river bund portion and Agri. Lands. = 25710 m
c) | Needamangalam BPT = 5.00 Lakh litres capacity.
13) | Gravity main
a) | From Needamangalam BPT to Thirupathur Tee point
b) | 1100 mm PSC main laid in the state high ways road and Clay Soil and river bund portion.=31500 m
14 | Gravity main
From Kottaiyur Branch point to Thiruvarur Municipality - 600 mm PSC main = 23160 m
Thiruvarur Booster sump - 11.00 Lakh litres capacity
| Pumpsets | 20.00 HP HSC pumpset duty 2840 Lpm X 21 m head.
25.00 HP HSC pumpset duty 2410 Lpm X 27 m head.
Gravity main
Thirupathur Tee point to Thiruthurai poondi booster
600 mm PSC main laid in the state high ways road and Clay Soil and river bund portion.=12000 m
Gravity main
Thirupathur Tee point to Edaiyur Sanganthi booster
900 mm PSC main laid in the centre of state high ways road - Soil made up of sandy and river bund portion and Agri. Lands.=15980 m
Gravity main
Edaiyur Sanganthi to Vanduvan cheri booster
800 mm PSC main laid in the state high ways road edge and river bund portion with PCB (problem)=13695 m
Thiruthuraipoondi Booster - 3.00 Lakh litres capacity
| Pumpsets | 20.00 HP HSC pumpset duty 2700 Lpm X 20 m head.
35.00 HP HSC pumpset duty 2719 Lpm X 35 m head.
Pumping main
Thiruthuraipoondi to Thainayuru= 19110 m
350 mm PSC main laid in ECR road - Soil made up of clay and Agri. Lands =19110 m
Thiruthuraipoondi to Melamaruthur
140 mm PVC to 63 mm PVC
Edaiyur Sanganthi Booster - 11.00 Lakh litres capacity
| Pumpsets | 60.00 HP HSC pumpset duty 4200 Lpm X 44 m head.
20.00 HP HSC pumpset duty 1664 Lpm X 20 m head.
Pumping main
Edaiyur Sanganthi to Muthupettai UTP= 15450 m
350 mm PSC main laid in ECR road - Soil made up of clay and Agri. Lands =26000 m
Pumping main
Edaiyur Sanganthi to Thondiakadu= 9500 m
350 mm PSC main laid in state highway road - Soil made up of clay and Agri. Lands =9500 m
Vanduvancheri Booster - 11.00 Lakh litres capacity
| Pumpsets | 90.00 HP HSC pumpset duty 5010 Lpm X 52 m head.
60.00 HP HSC pumpset duty 4225 Lpm X 45 m head.
45.00 HP HSC pumpset duty 4000 Lpm X 34 m head.
Pumping main
Vanduvan cheri booster to Vedaranyam Mpty
450 mm PSC main laid in the centre of state high ways road - Soil made up of sandy and river bund portion and Agri. Lands =25675 m
Pumping main
Vanduvan cheri booster to Kodiakarai = 26000 m
350 mm PSC main laid in the centre of state high ways road - Soil made up of sandy and river bund portion and Agri. Lands =26000 m
Pumping main
Vanduvan cheri booster to Pushpavanam = 31025 m
450 mm-350 mm PSC main laid in the centre of state high ways road - Soil made up of sandy and river bund portion and Agri. Lands =26000 m
14 | Feeder Main | 438 Kms
15 | No of Group sump with capacity | 104 sumps(10,000 litres to 2.50 lakhs litres.)
16 | Service Reservoirs with capacity | 397 (10000 litres to 1.00 LL )
17 | Separate power feeder main details | Provided at Headworks at Thiruvaikkavur. Booster stations at Thiruvarur, Edayur sanganthi,Thiruthuraipoondi, and Vanduvancheri
18 | Distribution system | 655 Km.

## Thiruvasaladi
SALIENT DETAILS
CWSS TO Thiruvasaladi and 9 other habitations in Kottur union
1 | Scheme Cost
a) | Installation cost | Rs.24.72 Lakh
b) | Annual Maintenance cost | Rs.9.31 Lakhs
2 | Administrative approval No&Amount | BP.Ms.No.338/Dt.06-03-1981 for Rs.24.72 Lakhs
3 | Technical sanction No & Amont
4 | Beneficiaries | 10 Habitations
5 | Populations | 2729
a) | Intermediate(Year) | ----
b) | Ultimate (Year) | -----
6 | Level of service | 40 lpcd
7 | Designed Quanity
a) | Present (Year) | 0.11 mld
b) | Intermediate (year) | ----
c) | Ultimate (Year) | ----
8 | Year of completion and Commissioning | 1983
a) | Original Scheme | original scheme
b) | Improvement Scheme
9 | Head works with Source details | Borewell at Radhanarasimmapuram
10 | Pumpset
a) | Type | submersible pumpset
b) | Duty | 300lpmX 50 M head
c) | Hours of Pumping | 10 Hours
11 | Treatment Plant (with Units Details) | ---
12 | Transmission Main
a) | Pumping Main | Pumping main - 10170 M
b) | Gravity Main | ----
13 | Booster Station | ----
a) | Sump with capacity | ----
b) | Pumpset details | ----
14 | Feeder Main | ----
15 | No of Group sump with capacity | ----
16 | Service Reservoirs with capacity | 6 Nos.
17 | Separate power feeder main details | ----
18 | Distribution system | 6580M

## Puthagaram
SALIENT DETAILS
CWSS TO Puthagaram and 20 other habitations in Kottur union of Thiruvarur district.
1 | Scheme Cost
a) | Installation cost | Rs.99.34 Lakhs
b) | Annual Maintenance cost | Rs.4.55 Lakhs
2 | Administrative approval No&Amount | Board Proc.No. F.Puthagaram /AE.2 /P&D 2005/Dt.21-11-2005 for Rs.96.70 Lakhs
3 | Technical sanction No & Amount | CE/ER/TNJ/ No.30/2005-06 Dt.19-12-2005 for Rs.99.34 Lakhs
4 | Beneficiaries | 21 Habitations
5 | Populations
a) | Present | 11882 (2011)
b) | Intermediate(Year) | 13072 = (2021) | 570320
c) | Ultimate (Year) | 14258 = (2036)
6 | Level of service | 40 lpcd
7 | Designed Quanity | 0.43 mld(2011)
a) | Present (Year) | 0.43 mld
b) | Intermediate (year) | ---
c) | Ultimate (Year) | ---
8 | Year of completion and Commissioning | 2008
a) | Original Scheme | ----
b) | Improvement Scheme | Improvement scheme
9 | Head works with Source details | Vedaranyam CWSS proposed for tapping from 11.00LL capacity sump at Edaiyur sanganthi
10 | Pumpset | Edaiyur sanganthi
a) | Type & Duty | sub.pumpset -2 Nos.
375lpm X 36 M (1 Standbye,1 working)10 HP
Nochiyur Samathuvapuram
submersible pumpset - 4 Nos.
300lpm X 22M (1 -standbye and 1 working)-7.5 H.P.
384 lpmX26m(1 standbye, 1 working)-7.5 HP
b) | Hours of Pumping | 20 Hrs from Edaiyur sanganghi to Nochiyur
12 Hrs from Nochiyur to Service Reservoirs
11 | Treatment Plant (with Units Details) | _____
12 | Transmission Main
a) | Pumping Main | 140mm KSC PVC pipe - 12350 M
b) | Gravity Main | ----
13 | Booster Station
a) | Sump with capacity | (1)Head work 11.00ll cap.sump at Edaiyur Sanganthi (existing)
(2)Nochiyur samathuvapuram sump - 2.00 LL capacity
14 | No of Group sump with capacity | 2 Nos.(1)11.00LL sump at Edaiyur sanganthi under VCWSS
2)2.00LL sump at Nochiyur Samathuvapuram
15 | Service Reservoirs with capacity | 20 Nos.
16 | Feeder Main | Branch pumping main.I and II 110mm PVC - 1044m; 90mm PVC-4562m; 75mm PVC-2224m: 63mm PVC-3435m; 50mm PVC-13505m
17 | Separate power feeder main details | Available at Edaiyur sanganthi under VCWSS
18 | Distribution system | 63MM PVC Pipe - 3940M

## boothamangalam
SALIENT DETAILS
CWSS TO Boothamangalam and 6 other habitations in Kottur union of Thiruvarur district.
1 | Scheme Cost
a) | Installation cost | Rs.24.25 Lakhs
b) | Annual Maintenance cost | Rs.9.00 Lakhs
2 | Administrative approval No&Amount | GO Ms No.390/Dt. 06-07- 1981
3 | Technical sanction No & Amont | CE(PH)No.23/81-82/ for Rs. 24.48 Lakhs
4 | Beneficiaries | 7 Habitations
5 | Populations | 2732
a) | Intermediate(Year) | ---
b) | Ultimate (Year) | ---
6 | Level of service | 40 lpcd
7 | Designed Quanity
a) | Present (Year) | 0.08 mld
b) | Intermediate (year) | ----
c) | Ultimate (Year) | ----
8 | Year of completion and Commissioning | 1983
a) | Original Scheme | Original scheme
b) | Improvement Scheme
9 | Head works with Source details | Bore well at Manakkarai
10 | Pumpset
a) | Type | submersible
b) | Duty | 250lpmX 50M head
c) | Hours of Pumping | 8 Hours
11 | Treatment Plant (with Units Details) | ---
12 | Transmission Main
a) | Pumping Main | (i)140mm OD PVC - 6800M
(ii)110mm - 3400M
b) | Gravity Main | ….Nil….
13 | Booster Station | ----
a) | Sump with capacity | ----
b) | Pumpset details | ----
14 | Feeder Main | ----
15 | No of Group sump with capacity | ----
16 | Service Reservoirs with capacity | 5 Nos.
17 | Separate power feeder main details | ----
18 | Distribution system | 6300M

## Sheet1
SALIENT DETAILS
CWSS TO VEDARANYAM
1 | Scheme Cost
a) | Installation cost | Rs.133.05 Crores
b) | Annual Maintenance cost | Rs.347.55 lakhs
2 | Administrative approval No&Amount | GO Ms No.11/MAWS/dt:28.1.2000 for RS.133.05 Crores
3 | Technical sanction No & Amont | CE/ER/TNJ/ No.55/99-2000 dt:3.2.200 for Rs.133.05 Crores
4 | Beneficiaries
THANJAVUR DISTRICT
56 Rural habitation in Kumbakonam and Papanasam union.
THIRUVARUR DISTRICT
Thiruvarur MPTY Muthupet UTP 364 Rural habitation inValangaiman,Needamangalam,Mannargudi,Kottur, Thiruthuraipoondi and Muthupet union.
NAGAPATTINAM DISTRICT
Vedaranyam MPTY,Thalainayur RTP,222 Rural habitation in Vedaranyam union.
5 | Populations
a) | Intermediate(Year) | 652318 (2011)
b) | Ultimate (Year) | 816500 (2026)
6 | Level of service | 90 lpcd, 70lpcd for TPs and 40lpcd for Rural Habs.
7 | Designed Quanity
a) | Present (Year) | 31.193 MLD - (2008)
b) | Intermediate (year) | 35.31 MLD - (2011)
c) | Ultimate (Year) | 43.59 MLD - (2026)
8 | Year of completion and Commissioning | 2004
a) | Original Scheme | Original Scheme
b) | Improvement Scheme | _____
9 | Head works with Source details | Collector well 2 Nos in River coleroon (Edaikudi and Thiruvaikkavur)
10 | Pumpset
a) | Type | Vertical Turbine Pumpset.
b) | Duty | 14365 lpm X18m(80HP)- 1 No. each in Collector wells
c) | Common sump at Thiruvaikavur. | 11.00 Lakh litres capacity.
14365 lpm X 35m(150 HP)-8m dia common sump.
2 Nos.of totally 300 HP runing in parallal
11 | Hours of Pumping | 20 Hrs.
a) | Pumping main
b) | From Head work to Nallur BPT
c) | 900 mm PSC main laid in the centre of road - Soil made up of sandy and sugar cane carriying roads = 8790 m
d) | Nallur BPT = 5.00 Lakh litres capacity
12 | Gravity main
a) | From Nallur BPT to Needamangalam BPT
b) | 1100 mm PSC main laid in the centre of state high ways road = 25710 m
c) | Needamangalam BPT = 5.00 Lakh litres capacity.
13) | Gravity main
a) | From Needamangalam BPT to Thirupathur Tee point
b) | 1100 mm PSC main laid in the state high ways road =31500 m
14 | Gravity main
a) | From Kottaiyur Branch point to Thiruvarur Municipality - 600 mm PSC main = 23160 m
b) | Thiruvarur Booster sump - 11.00 Lakh litres capacity
c) | Pumpsets | 20.00 HP HSC pumpset duty 2840 Lpm X 21 m head.
25.00 HP HSC pumpset duty 2410 Lpm X 27 m head.
15 | Gravity main
a) | Thirupathur Tee point to Thiruthurai poondi booster
b) | 600 mm PSC main laid in the state high ways road =12000 m
16 | Gravity main
Thirupathur Tee point to Edaiyur Sanganthi booster
900 mm PSC main laid in the centre of state high ways road =15980 m
17 | Gravity main
a) | Edaiyur Sanganthi to Vanduvan cheri booster
b) | 800 mm PSC main laid in the state high ways road =13695 m
c) | Thiruthuraipoondi Booster - 3.00 Lakh litres capacity
d) | Pumpsets | 20.00 HP HSC pumpset duty 2700 Lpm X 20 m head.
35.00 HP HSC pumpset duty 2719 Lpm X 35 m head.
18 | Pumping main
a) | Thiruthuraipoondi to Thainayuru
b) | 350 mm PSC main laid in ECR road =19110 m
c) | Thiruthuraipoondi to Melamaruthur
d) | 140 mm PVC to 63 mm PVC
e) | Edaiyur Sanganthi Booster - 11.00 Lakh litres capacity
f) | Pumpsets | 60.00 HP HSC pumpset duty 4200 Lpm X 44 m head.
20.00 HP HSC pumpset duty 1664 Lpm X 20 m head.
20 | Pumping main
a) | Edaiyur Sanganthi to Muthupettai UTP= 15450 m
b) | 350 mm PSC main laid in ECR road =26000 m
c) | Pumping main
d) | Edaiyur Sanganthi to Thondiakadu= 9500 m
e) | 350 mm PSC main laid in state highway road =9500 m
f)
g) | Vanduvancheri Booster - 11.00 Lakh litres capacity
h) | Pumpsets | 90.00 HP HSC pumpset duty 5010 Lpm X 52 m head.
60.00 HP HSC pumpset duty 4225 Lpm X 45 m head.
45.00 HP HSC pumpset duty 4000 Lpm X 34 m head.
21 | Pumping main
a) | Vanduvan cheri booster to Vedaranyam Mpty
b) | 450 mm PSC main laid in the centre of state high ways road =25675 m
22 | Pumping main
a) | Vanduvan cheri booster to Kodiakarai = 26000 m
b) | 350 mm PSC main laid in the centre of state high ways road =26000 m
c) | Pumping main
d) | Vanduvan cheri booster to Pushpavanam = 31025 m
e) | 450 mm-350 mm PSC main laid in the centre of state high ways road =26000 m
23 | Feeder Main | 438 Kms
24 | No of Group sump with capacity | 104 sumps(10,000 litres to 2.50 lakhs litres.)
25 | Service Reservoirs with capacity | 397 (10000 litres to 1.00 LL )
26 | Separate power feeder main details | Provided at Headworks at Thiruvaikkavur. Booster stations at Thiruvarur, Edayur sanganthi,Thiruthuraipoondi, and Vanduvancheri
27 | Distribution system | 655 Km.