## Slide 1
: Project Area
Valliyoor
Radhapuram
Palayamkottai
Ambasamudaram
Chermadevi
Vasudevanallur
Headworks at Pathamadai
Singikulam
S. Vijayanarayanam
Thisyanvilai
Kalakadu
Vadakkankulam
Avaraikulam
RIVER TAMBIRAPARANI
Mavadi
Sankarankovil
Kuruvikulam
Kadayanallur
Melaneelithanallur
Shenkottai
Thenkasi
Alangulam
Keelapavoor
Manur
Kadayam
Pappakudi
Tirunelveli
Kalakadu
Radhapuram
Samugarengapuram
Shanmugapuram
Ittamozhi
Pettaikulam
Perumalnagar
Nanguneri
Pattarkattivilai
Moolaikadu
Pumping station
Marugalkuruchi
Nanguneri
AUGMENTATION OF EXISTING CWSS TO NANGUNERI – TISAYANVILAI TPS & 297 HABS INCLUDING KALAKKADU TP IN TIRUNELVELI DISTRICT.
INDEX PLAN
Manimutharkulam
Alaganeri

## Slide 2
AUGMENTATION OF CWSS TO NANGUNERI, THISAYANVILAI TPS AND 297 WAYSIDE HABITATIONS INCLUDING WSIS TO KALAKAD TP
N
E
Mukkudal
Tirunelveli
Kodaganallur
Cremation Yard
Existing Nanguneri Thisayanvilai CWSS Pumphouse near pathamadai
Existing Sudalai Temple Karisoolnthmangalam
FS
MS
CS
MS
2
1
0.30
1.1
PB
IW I 4.40m
CS
MS
FS
0.10
3.80
0.60
PB
IW 2 4.50m
CS
MS
4.0
0.60
PB
IW 3 4.60m
CS
MS
3.7
1.05
PB
IW 4 4.75m
CS
MS
FS
0.15
2.50
2.0
PB
IW 5 4.65m
CS
MS
3.70
0.85
PB
IW 6 4.55m
MS
5.00
PB
IW 7 5.00m
MS
5.00
PB
IW 8 5.00m
I W NO | Well NO 10 of Ngi CWSS |  | Well for Nadukallur | 
 | Bearing | Distance | Bearing | Distance
1 | 3170 | 65 | 90 | 37
2 | 3270 | 45 | 560 | 45
3 | 140 | 41 | 590 | 85
4 | 93.5 | 120 | 970 | 205
5 | 980 | 150 | 1020 | 235
6 | 960 | 215 | 990 | 300
7 | 860 | 172 | 880 | 257
8 | 920 | 255 | 950 | 340
IW.No.10 of NGI CWSS
1
2
3
4
6
7
8
IW.No. 9 of NGI CWSS
IW.- of Nadulkallur WSS
Depth
120
108
172
76
From NGI IW No 10 to IW for Nadukalloor
Distance 72m Bearing 1090
41
33
72
45
36
33
41
78
65
37
Existing Infiltration Wells
Proposed Infiltration Wells
38
270 M
Reference Wells
Selected Points 2 to 8
5

## Slide 3
CWSS TO NANGUNERI – TISAYANVILAI TPS & 297 HABS INCLUDING KALAKKADU TP IN TIRUNELVELI DISTRICT.
FLOW DIAGRAM
Sump @ Manimutharkulam
L:20M LWL:70.065 GL:71.065
MWL:72.065
10
Sump cum p’room@ Marukalkurichi L:52M
LWL:99.885GL:100.885 MWL:101.885
15
Sump cum p’room@
Nanguneri L:3165 M
LWL:97.430 GL:98.930
MWL:99.430
Sump @ Mavadi
E P
LWL:75.415 75.915
GL:77.415 77.415
MWL:78.915 78.915
10
Sump @ Perumalnagar L:245 M
LWL:75.150 GL: 75.550
MWL:77.150
100
Sump @ S.Vijayanarayanam
LWL:50.030 GL: 52.530
MWL:53.030
LS:8330
GL:76.720
250
Sump(P) @ Pathamadai
LWL:42.015 GL: 47.015
MWL:51.015
To Cheranmahadevi
To Palayamkottai
5
Sump @ Moolaikadu
L:30M LWL:68.455GL:69.745
MWL:71.455
Sump cum p’room@
Avaraikulam L:4410 M
LWL:45.270 GL:46.770
MWL:48.270
10
Sump cum p’room@
Shanmugapuram
LWL:84.600
GL:86.205
MWL:86.600
100
Sump @ Radhapuram
LWL: 45.475
GL: 47.475
MWL:48.475
50
Sump @ Vadakkankulam
LWL:54.410 GL: 55.410
MWL:56.910
10
15
Sump cum p’room@
Shamugarengapuram
L:30M LWL:48.780 GL:50.280
MWL:51.780
10
Sump cum p’room@
Pattarkattivilai L:150 M
LWL:40.045 GL:41.400
MWL:42.045
10
Sump cum p’room@
Ittamozhi LWL:34.650
GL:36.455
MWL:36.650
50
Sump @ Tisayanvilai
LWL:21.320 GL:22.820
MWL:23.820
10
Sump cum p’room@
Pettaikulam L:4325 M
LWL:23.175 GL:24.675
MWL:25.175
LS:9740
GL:71.040
LS:3900
LS:17950
GL:51.530
LS:5400
GL:42.575
LS:13500
LS:14990
LS:14820
GL:68.675
LS:0
LS:5070
GL:68.645
LS:4050
GL:70.905
LS:9000
GL:51.280
LS:16480
LS:7860
LS:5450
5228/5774
To Meenavankulam
Gr4-99/107(4)
To Nedunkulam
Gr3-187/203(13/2)
To Perumal Thoppu
Gr5-156/169(9)
4539/5164
255/276
To Rajiv gandhi nagar
Gr2-162/170(11/9)
30
400
250
500
200
60
350/
371
To Keelakarankadu
Gr6-79/82(7/3)
To Thoranakurichi
Gr7-85/90(6/1)
To Alankulam
Gr8-186/199(12/4)
100
LS:18000
To Savalaikarankulam
Gr27-145/155(10/1)
To Parappadi
Gr26-120/128(7)
To N.Vijayanarayanam
Gr28-251/275(10/6)
To Tharagankadu
Gr29-177/189(10/4)
2172/
2504
60
291/
312
To Thuvarampadu
Gr32-116/122(8/2)
To Sankanankulam(H)
Gr33-175/190(9/4)
342/371
3253/
3486
150
60
51/
53
To Moolaikadu
Gr11-64/66(5/1)
2893/
3102
To Pulikualm(H)
Gr12-362/390(12/1)
To Seelathikualm
Gr13-310/333(13/2)
To A.Thirumalapuram
Gr14-136/146(5/1)
200
791/
857
2102/
2245
400
To Subramaniaperi
Gr15-302/328(12/7)
To Kattalaicheri(H)
Gr16-125/138(5/1)
To Chidambarapuram
Gr25-218/237(5)
300
To Betharengapuram
Gr18-129/137(6/4)
To Uralvoimozhi colony
Gr22-250/269(12/3)
To Madanadar kudiyiruppu
Gr19-104/107(5/2)
To Kavalkinaru vilakku
Gr20-197/199(11/2)
To Vadakkankulam
Gr21-203/208(6/3)
840/
912
To Avaraikulam
Gr24-222/242(6)
LS:11250
GL:31.570
1881/2192
1579/
1869
60
302/
323
60
To Vadalivilai
Gr30-175/190(8)
To Thinakarankulam
Gr34-227/243(12/7)
To Rammathapuram(S)
Gr35-75/80(4/1)
To Kamaraj Nagar
Gr36-68/71(6)
IW – 7 No.s(N)
IW – 14 No.s(E)
RIVER TAMBIRAPARANI
100
Nanguneri TP
727/895
Thisayanvilai TP
1398/1678
KALAKADU TP
1683/2074
Sump @ Kalakadu
LS:13110 LWL:116.200
GL: 117.700 MWL:119.200
150
727/895
To Kandiaperi
Gr9-223/239(15)
86/92
3030/
3247
To Nallankulam
Gr10-86/92(6)
1473/1563
To Erumbucheri
Gr17-202/216(11/8)
2944/
3155
3557/3993
3207/3622
LS:8130
LS:0
27/29
500 PSC
500 PSC
500 PSC
400AC
250 AC
250 AC
200 AC
LS:6870
140 PVC
110 PVC
350 CI,300CI
300AC
300AC
200AC
LS:3100
150AC
140 PVC
300AC
300AC
110 PVC
90 PVC
140 PVC
90 PVC
400AC
5201/5745
4623/5352
10
Sump @ Singikulam
LS:14850 LWL:67.420
GL: 69.420 MWL:70.920
4623/5352
LS:11580
GL:101.010
100
Sump @ Alaganeri
LWL:45.270 GL:46.770
MWL:48.270
Hump at
LS:12330
GL:104.240
To Manimutharkulam
Gr1-27/29(2)
110 PVC
To Palavoor
Gr23-150/164(2)
To Ittamozhi
Gr31-167/181(6)
To Suvishesapuram
Gr37-113/120(6)
LS:3180
GL:58.340
60
L:570 M
400 PSC
350 PSC
10
60
3253/
3486
400/433
Sump (E)@ Pathamadai
LWL:43.015 GL: 47.015
MWL:50.015
Elevated sump L:30 LWL:102.500
GL:100.885MWL:105.000

## Slide 4
Existing Pumping main from Sump at Head works to Sump at Singikulam
Sump @ Singikulam
LS:14850 LWL:67.420
GL: 69.420 MWL:70.920
250
Sump(E)@ Pathamadai
LWL:43.015 GL: 47.015
MWL:50.015
To Cheranmahadevi
To Palayamkottai
LS:14820
GL:68.675
400
250
500
Head Works:
Sump cum pumproom :2.50 LL, 6.75 m dia [Existing]
Control room : 12 m x 7 m [Existing]
Pump set : 90 HP turbine x 7230 lpm x 39 m [Existing]
7.5 HP Sub x 725 lpm x 15 m head – 9 Nos.[Existing]
Pumping main:
Sump @ Head works to Sump @ Singikulam
0 to 3405 m : 500 PSC 12 Ksc [Existing]
3405 m to 3605 m : 500 CI LA [Existing]
3605 m to 8850 m : 500 PSC 12 Ksc [Existing]
8850 m to 14850 m : 500 PSC 4 Ksc [Existing]
Branch to Prop.Sump @ Manimutharkulam
0 to 20 m : 50 mm GI Medium [Proposed]
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and
297 way side Habitations
including Kalakadu TP in Tirunelveli District
Flow Diagram
IW – 7 No.s(P)
IW – 9 No.s(E)
RIVER TAMBIRAPARANI
5228/5774
5201/5745
IW – 1 No. (E)
LS:9740
GL:71.040
27/29
10
To Manimutharkulam
Gr1-27/29(2)
Sump @ Manimutharkulam
L:20M LWL:70.065 GL:71.065
MWL:72.065

## Slide 5
Proposed Pumping main from Head works to Sump at Singikulam
Sump @ Singikulam
LS:14850 LWL:67.420
GL: 69.420 MWL:70.920
250
To Cheranmahadevi
To Palayamkottai
LS:14820
GL:68.675
400
250
500
Head Works:
Sump Cum Pumproom:4.00 LL, [Proposed]
Control room : 12 m x 7 m [Existing]
Pump set : 100 HP turbine x 4623 lpm x 48 m [Proposed]
7.5 HP Sub x 725 lpm x 15 m head – 1 No.[Existing]
5 HP sub x 580 lpm x 16 m head – 7 Nos([Proposed)
Pumping main:
Sump @ Head works to Sump @ Singikulam
0 to 3405 m : 400 PSC 10 Ksc [Proposed]
3405m to 5760m : 400PSC 8 Ksc [Proposed]
5760 m to 9090 m : 400 PSC 8 Ksc [Proposed]
9090 m to 14850 m : 400 PSC 4 Ksc [Proposed]
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and
297 way side Habitations
including Kalakadu TP in Tirunelveli District
Flow Diagram
IW – 7 No.s(P)
IW – 10 No.s(E)
RIVER TAMBIRAPARANI
4623/5352
4623/5352
Sump(P) @ Pathamadai
LWL:42.015 GL: 47.015
MWL:51.015

## Slide 6
Sump @ Singikulam
LS:0 LWL:67.420
GL: 69.420 MWL:70.920
15
Sump cum p’room@
Nanguneri L:3165 M
LWL:97.430 GL:98.930
MWL:99.430
10
Sump @ Perumalnagar L:245 M
LWL:75.150 GL: 75.550
MWL:77.150
100
Sump @ S.Vijayanarayanam
LWL:50.030 GL: 52.530
MWL:53.030
LS:17950 m
GL:51.530
LS:30 m
GL:68.675
KALAKADU TP
1683/2074
4539/5164
727/895
To Rajiv gandhi nagar
Gr2-162/170(11)
250
500
200
60
350/
371
To Keelakarankadu
Gr6-79/82(7)
To Thoranakurichi
Gr7-85/90(6)
To Alankulam
Gr8-186/199(12)
100
LS:18000 m
35573993
Nanguneri TP
727/895
Booster station @ Singikulam
Sump :2.50 LL, 9.60 m dia [Existing]
5.00 LL13.50 m dia [Proposed]
Pump room : 10 m x 8 m [Existing], 8 m x 5 m [Proposed]
Pump set : 90 HP Cent x 4539 lpm x 45 m [Existing]
: 45 HP Cent x 1683 lpm x 59 m [Proposed] [Kalakadu TP]
Pumping main from Sump @ Singikulam to Hump point
0 m to 30 m : 500 CI LA [Existing]
30 m to 2550 m : 500 PSC 12 Ksc [Existing]
2550 m to 8910 m : 500 PSC 8 Ksc [Existing]
8910 m to 12330 m : 500 PSC 4 Ksc [Existing]
Branch main from Hump point to sump at South Vijayanarayanam
0 m to 2120 m : 500 PSC 4 Ksc[Existing]
2120 m to 4250 m : 400 AC cl 10 [Existing]
4250 m to 4290 m : 400 CI LA [Existing]
4290 m to 8330 m : 400 AC cl 10 [Existing]
8330 m to 13820 m : 300 AC cl 10 [Existing]
13820 m to 13920 m : 300 CI LA [Existing]
13920 m to 15230 m : 300 AC cl 10 [Existing]
15230 m to 15400 m : 250 AC cl 10 [Existing]
15400 m to 15460 m : 250 CI LA [Existing]
15460 m to 17870 m : 250 AC cl 10 [Existing]
17870 m to 17920 m : 250 CI LA [Existing]
17920 m to 18000 m : 250 AC cl10 [Existing]
Pumping main from Singikulam to Prop. Sump @ Kalakadu
0 m to 2000 m : 350 PSC 14 Ksc [Proposed]
2000 m to 5000 m : 350 PSC 12 Ksc [Proposed]
5000 m to 7000 m : 350 PSC 8 Ksc [Proposed]
7000 m to12000 m : 350 PSC 6 Ksc [Proposed]
12000 m to 13110 m : 350 PSC 4 Ksc [Proposed]
Booster station @ Kalakadu
Sump :150 LL, 8.00 m dia [Proposed]
Pump room : 3 m x 3 m [Proposed]
Stand post @ Marukalkuruchi
Stand post : 30000 lit [ Existing]
Branch to Stand post @ Marukalkuruchi
0 m to 30 m : 100 CI LA [Existing]
Booster station @ Marukalkuruchi
Sump : Sump cum pump house, 10000 lits [Existing]
Brnach main to Sump @ Nanguneri
0 m to 2970 m : 250 AC Cl 15 [Existing]
2970 m to 3165 m : 200 AC Cl 10 [Existing]
Booster station @ Nanguneri
Sump : Sump cum pump house, 15000 lits [Existing]
Sump, 200000 lits [Proposed]
Branch to Sump @ Perumal nagar
0 m to 245 m : 90 PVC 4 Ksc [Existing]
Booster station @ Perumal nagar
Sump : Sump, 10000 lits [Existing]
Sump, 60000 lits [Proposed]
AUGMENTATION OF EXISTING CWSS TO NANGUNERI – THISAYANVILAI TPS
AND 297 HABS INCLUDING KALAKKADU TP IN TIRUNELVELI DISTRICT.
150
1683/
2074
Flow Diagram
To Nedunkulam
Gr3-187/203(13)
Sump @ Kalakadu
LS:13110 LWL:116.200
GL: 117.700 MWL:119.200
3207/3622
LS:8330
GL:76.720
Pumping main from Sump at Singikulam to sump at South Vijayanarayanam
3207/3622
10
Sump cum p’room@ Marukalkurichi L:52M
LWL:99.885GL:100.885 MWL:101.885
To Meenavankulam
Gr4-99/107(4)
To Perumal Thoppu
Gr5-156/169(9)
255/276
30
LS:11580
GL:101.010
Hump at
LS:12330
GL:104.240
Elevated sump L:30 LWL:102.500
GL:100.885MWL:105.000

## Slide 7
Sump @ Singikulam
LS:0 LWL:67.420
GL: 69.420 MWL:70.920
LS:30 m
GL:68.675
250
500
3253/3486
150
100
Booster station @ Singikulam
Sump :2.50 LL, 9.60 m dia [Existing]
5.00 LL13.50 m dia [Proposed]
Pump room : 10 m x 8 m [Existing], 8 m x 5 m [Proposed]
Pump set : 75 HP Cent x 3253 lpm x 52 m [Proposed]
Pumping main from Sump @ Singikulam to Hump point
0 m to 2550 m : 350 PSC 12 Ksc [Proposed]
2550 m to 8910 m : 350 PSC 8 Ksc [Proposed]
8910 m to 12330 m : 350 PSC 4 Ksc [Proposed]
Branch main from Hump point to sump at Mavadi
0 m to 8330 m : 350 PSC 6 Ksc [Proposed]
8330 m to 12330 m : 400 AC cl 10 [Existing]
Booster station @ Mavadi
Sump : Sump, 150000 lits [Existing]
Sump, 100000 lits [Proposed]
AUGMENTATION OF EXISTING CWSS TO NANGUNERI – THISAYANVILAI TPS
AND 297 HABS INCLUDING KALAKKADU TP IN TIRUNELVELI DISTRICT.
Flow Diagram
LS:12330
GL:104.240
LS:8330
GL:76.720
Pumping main from Sump at Singikulam to sump at Mavadi
3253/3486
Sump @ Mavadi
E P
LWL:75.415 75.915
GL:77.415 77.415
MWL:78.915 78.915

## Slide 8
AUGMENTATION OF EXISTING CWSS TO NANGUNERI – TISAYANVILAI TPS & 297 HABS INCLUDING KALAKKADU TP IN TIRUNELVELI DISTRICT.
FLOW DIAGRAM
5
Sump @ Moolaikadu
L:30M LWL:68.455GL:69.745
MWL:71.455
10
100
Sump @ Radhapuram
LWL: 45.475
GL: 47.475
MWL:48.475
50
10
Sump cum p’room@
Shamugarengapuram
L:30M LWL:48.780 GL:50.280
MWL:51.780
LS:0
LS:5070 m
GL:68.645
LS:4050 m
GL:70.905
LS:9000 m
GL:51.280
LS:16480 m
LS:7860 m
150
60
To Kandiaperi
Gr9-223/239(15)
86/
92
3030/
3247
To Nallankulam
Gr10-86/92(6)
51/
53
2944/
3155
To Moolaikadu
Gr11-64/66(5)
2893/
3102
To Pulikualm(H)
Gr12-353/383(12)
To Seelathikualm
Gr13-302/327(13)
To A.Thirumalapuram
Gr14-136/147(5)
200
791/
857
2102/
2245
400
To Subramaniaperi
Gr15-302/328(12)
To Kattalaicheri(H)
Gr16-125/138(5)
300
1473/1563
To Betharengapuram
Gr18-129/137(6)
To Madanadar kudiyiruppu
Gr19-104/107(5)
To Kavalkinaru vilakku
Gr20-197/199(11)
To Vadakkankulam
Gr21-203/208(6)
590/
643
To Erumbucheri
Gr17-202/216(11)
Booster station @ Mavadi
Sump :1.50 LL, 7..50 m dia [Existing]
1.00 LL, 6.00 m dia [Proposed]
Pump room : 10 m x10 m [Existing],
Pump set : 60 HP Cent x 3525 lpm x 37m [Existing]
Pumping main from Sump @ Mavadi to Sump @ Shanmugapuram
0 m to 910 m : 350 CI LA [Existing]
910 m to 1500 m : 300 CI LA [Existing]
1500 m to 5070 m : 300 AC cl10 [Existing]
5070 m to 8130 m : 90 PVC 4 Ksc [Existing]
Branch to Sump @ Radhapuram
0 to 16480 m : 300 AC cl10 [Existing]
Booster station @ Shanmugapuram:
Sump : Sump cum pump house, 10000 lts, 2.50 m dia [Existing]
Sump :10000 lts [Proposed]
Branch to Sump @ Moolakadu
0 to 30 m : 63 PVC 4 Ksc [Existing]
Booster station @ Moolakadu:
Sump : Sump, 5000 lts, 1.50 m dia [Existing]
Pump house : 1.5 m x 1.5 m [existing]
Branch to Sump @ Samugarengapuram
0 m to 30 m : 90 PVC 4 Ksc [Existing]
Booster station @ Samugarengapuram:
Sump : Sump cum Pump house, 10000 lits, 2.00 m dia [Exist]
Sump, 200000 lts, 3.50 m dia [Proposed]
Pump house : 3 m x 3 m [Existing]
Booster station @ Radhapuram:
Sump : Sump, 100000 lts, 6.50 m dia [Existing]
Sump, 400000 lts, [Proposed]
Pump house : 12 x 8 m [Existing]
Pump set : 30 HP Cent x 1445 lpm x 45 m Existing]
Pumping main from Radhapuram to Sump @ Vadakkankulam
0 m to 7860 m : 200 AC cl10 [Existing]
Booster station @ Vadakkankulam
Sump : Sump, 50000 lits, 4.60 m dia [Existing]
Sump, 300000 lits, 5.00 m dia [Proposed]
Pump house : 10 m x 8 m [ Existing]
Pump set : 12.5 HP x 700 lpm x 46m [Existing]
Pumping main from Sump @ Vadakkankulam to Sump @ Alaganeri
0 m to 600 m : 150 AC cl 15 [Existing]
600 m to 3100 m : 150 AC cl10 [Existing]
3100 m to 5450 m : 110 PVC 4 Ksc [Proposed]
Branch main to Avaraikulam sump 1 & 2
To sump 1
0 m to 4410m :140 PVC 4Ksc [Existing]
To sump 2
0 m to 30 m :90 PVC 4 Ksc[Proposed]
30 m to 570 m :90 PVC 4 Ksc [Existing]
Booster station 1 @ Avaraikulam
Sump : Sump cum pump house, 15000 lits, 3.00 m dia [Existing]
Sump : 60000 lts [Proposed]
Booster station 2 @ Avaraikulam
Sump : Sump 60000 lits, [Proposed]
Booster station at Alaganeri Sump:100000 lts [Proposed]
LS:8130 m
LS:0
LS:0
10
LS:5450
100
Sump @ Alaganeri
LWL:45.270 GL:46.770
MWL:48.270
To Palavoor
Gr23-150/164(2/1)
Sump cum p’room@
Avaraikulam L:4410 M
LWL:46.445 GL:47.945
MWL:48.445
15
To Chidambarapuram
Gr25-218/237(5/1)
To Avaraikulam
Gr24-222/242(6)
60
Sump cum p’room@
Avaraikulam 2 L:570 M
LWL:44.260 GL:45.760
MWL:47.260
To Uralvoimozhi colony
Gr22-250/269(12/3)
60
Sump @ Mavadi
E P
LWL:75.415 75.915
GL:77.415 77.415
MWL:78.915 78.915
Sump cum p’room@
Shanmugapuram
LWL:84.600
GL:86.205
MWL:86.600
Sump @ Vadakkankulam
LWL:54.410 GL: 55.410
MWL:56.910

## Slide 9
100
Ex. Sump & Prop. Sump @ S.Vijayanarayanam
LWL:50.030 GL: 52.530 MWL:53.030
10
Ex. Sump cum p’room & Prop. Sump
@ Pattarkattivilai L:150 M
LWL:40.045 GL:41.400
MWL:42.045
10
Sump cum p’room &
Prop. Sump @ Ittamozhi
LWL:34.650 GL:36.455
MWL:36.650
50
Ex. Sump & Prop. Sump
@ Tisayanvilai
LWL:20.820 GL:22.820
MWL:23.820
10
LS:5400 m
GL:42.575
LS:13500
LS:14990 m
150
LS:0 m
To Savalaikarankulam
Gr27-145/155(10)
To Parappadi
Gr26120/128(7)
To N.Vijayanarayanam
Gr28-251/275(10)
To Tharagankadu
Gr29-177/189(10)
2172/
2504
60
291/
312
To Thuvarampadu
Gr32-116/122(8)
To Sankanankulam(H)
Gr33-175/190(9)
342/371
LS:11250 m
GL:31.570
1881/2192
1579/
1869
60
302/
323
60
To Vadalivilai
Gr30-175/190(8)
To Ittamozhi
Gr31-167/181(6)
To Thinakarankulam
Gr34-227/243(12)
To Rammathapuram(S)
Gr35-75/80(4)
To Thangammalpuram
Gr36-68/71(6)
100
Thisayanvilai TP
1398/1678
Booster station @ South Vijaya Narayanam
Sump :1.00 LL, 6.50 m dia [Existing]
1.00 LL, 8.00 m dia [Proposed]
Pump room : 10 m x 8 m [Existing],
Pump set : 30 HP Cent x 1960 lpm x 33 m [Existing]
:7.5 HP Cent x 450lpm x 28m [Existing]
Pumping main from Sump @ S.V. Narayanam to Sump @ Ittamozhi
0 m to 2850 m :1460 PVC 6 Ksc [Proposed]
2850 m to 6870 m : 140PVC 4 Ksc [Existing]
6870 m to 13500 m : 110 PVC 4 Ksc [Existing]
Booster station @ Ittamozhi:
Sump : Sump cum pump house, 10000 lts [Existing]
Sump, 100000 lts,[Proposed]
Pump main from Sump @ S.V. Narayanam to Sump @ Thisayanvilai
0 m to 11250 m : 250 AC Cl 10 [Existing]
11250 m to 12580 m : 200 AC Cl 10 [Existing]
12580 m to 12700 m : 200 CI LA [Existing]
12700 to 14990 m : 200 AC cl10 [Existing]
Booster station @ Thisayanvilai:
Sump : Sump, 50000 lts [Existing]
Sump, 60000 lts [Proposed]
Pump house : 8 m x 6 m [Existing]
Branch to Sump @ Patterkattivilai
0 m to 150 m : 90 PVC 4 Ksc [Existing]
Booster station @ Patterkattivilai:
Sump : Sump cum Pump house, 10000 lits [Existing]
Sump, 60000 lts [Proposed]
Branch to Sump @ Pettaikulam
0 m to 4325 m : 140 PVC 4 Ksc [Existing]
Booster station @ Pettaikulam:
Sump : Sump cum pump house, 10000 lts [Existing]
Sump, 60000 lts [Proposed]
LS:1460 m
AUGMENTATION OF EXISTING CWSS TO NANGUNERI – TISAYANVILAI TPS AND 297 HABS INCLUDING KALAKKADU TP IN TIRUNELVELI DISTRICT.
Flow Diagram
To Suvishesapuram
Gr37-113/120(6)
Sump cum p’room@
Pettaikulam L:4325 M
LWL:23.175 GL:24.675
MWL:25.175

## Slide 10
GROUP - 1
Details
No. Habitations : 2
No. of Panchayat : 2
No. of Service Reservoirs: 2
[ Existing – 1, Proposed – 1]
Sump @ Manimutharkulam to Prop. SR @ Manimutharkulam
SR @ Muthu Veerappapuram
.GL : 66.850 MWL : 74.850
SR (P) @ Manimutharkulam
GL: 67.265 MWL: 75.265
10
10
10
Booster Station @ Manimutharkulam
Prop..Sump and Control room 1.5 m x 1.5 m
GL : 71.065 m
LWL: 70.065 m
MWL: 72.065 m
LS 20 M
71.065
L: 1170 M
LS 670 M
LS 660 M
68.850
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District
Pump set:
1 HP Sub x 34 lpm x 9 m [Proposed]
Pumping main:
Sump @ Manimutharkulam to Prop.SR @ Manimutharkulam
0 to 20 m : 63 PVC 4 Ksc [Proposed]
20 m to 1170 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ SR @ Muthuveerappapuram
0 m to 660 m : 63 PVC 4 Ksc [Proposed]
660 m to 670 m : 63 PVC 4 Ksc [Existing]
27/ 29
34 / 36
12/ 13
15 / 16
15/ 16
19 / 20

## Slide 11
Existing Sump & Prop. Sump
@ Singikulam
GL: 69.420 LWL: 67.420 MWL: 70.920
30
SR @ Vaduvoorpatti
L:5430M GL:63.405
MWL:71.905
30
SR @ Singikulam
L:180M GL: 71.960
MWL:82.460
SR @Thennerkulam
& Melkarai
L:1380 m GL: 74.575
MWL:83.075
SR @ Malaiyadicheri H
L: 10 M GL: 73.155 MWL; 83.655
SR @ Elayamuthur(N)
GL:65.060 MWL:73.060
SR @ Bethenia
L:15M GL:70.750
MWL:79.250
SR @ Thachankulam
L:345 M GL:74.010
MWL:82.010
10
SR (P)@ Rajiv Gandhi Nagar
GL:76.805 MWL:84.805
SR(P) @ Selvapudukulam
L:30M GL:68.195 MWL:76.195
60
60
10
30
10
10
LS:30 m
GL:68.800
LS:1090 m
GL:73.350
LS:1140 m
GL:73.455
LS:2460 m
GL:82.265
LS:500 m
GL:70.940
LS:750 m
GL:72.675
LS:2130 m
LS:4560 m
GL:70.750
LS:5370 m
GL:68.195
LS:6450 m
10
SR(P) @ Elayamuthur(S)
L:110M GL:68.355 MWL:76.355
LS:0 m
LS:0 m
LS:0 m
LS:0 m
LS:5580 m
GL:68.340
LS:0 m
250
500
162/ 170
66/ 70
43/ 46
33/ 36
10/ 10
10/ 10
13/ 14
14/ 15
10/ 10
24/ 25
10/ 10
34/ 35
10/ 10
44/ 45
32/ 35
10/ 10
54/ 55
86/ 90
10/ 10
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District
GROUP - 2
Details
No. Habitations : 11
No. of T Panchayat : 3
No. of Service Reservoirs: 10
[ Existing – 7, Proposed – 3]
Sump @ Singikulam to Prop. SR @ Rajiv Gandhi Nagar
Pump set:
3 HP Subt x 162 lpm x 33 m [Proposed]
Pumping main:
Sump @ Singikulam to Prop. SR @ Rajiv Gandhi Nagar
0 to 30 m : 90 PVC 4 Ksc [Proposed]
30 m to 750 m : 50 GI [Existing]
750 m to 2130 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Elayamuthur North
0 m to 2460 m : 63 PVC 4 Ksc [Proposed]
2460 m to 4560 m : 63 PVC 6 Ksc [Existing]
4560 m ro 6450 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Vaduvoorpatti
0 m to 3380 m : 50 PVC 6 Ksc [Existing]
3380 m to 5310 m : 75 PVC 4 Ksc [Existing]
5310 m to 5430 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Melkarai & Theneerkulam
0 m to 1380 m : 50GI [Existing]
Branch to.SR @ Singikulam
0 m to 180 m : 50 GI [Existing]
Branch to SR @ Malayadicheri H
0 m to 10 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Thachankulam
0 m to 345 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Bethania
0 m to 15 m : 63 PVC 4 Ksc [Existing]
Branch to Prop. SR @ Selvavinayagapuram
0 m to 30 m : 63 PVC 4 Ksc [Proposed]
Branch to Prop. SR @ Elayamuthue South
0 m to 110 m : 50 PVC 6 Ksc [Proposed]

## Slide 12
GROUP - 3
Sump @ Singikulam
GL: 69.420 LWL: 67.420 MWL: 70.920
SR @ Poolam
L:900M GL: 77.125
MWL:85.125
SR @ Mudalaikulam Nadar Colony
L:75 M GL: 89.500 MWL:98.500
SR @ Panankulam
L: 30 M GL: 86.530 m
MWL: 97.030
SR @ Thalaikulam
Reddiar Qts
L:30M GL:93.340
MWL:101.840
To Nanguneri
SR @ Mudalaikulam Maravar Colony
L:140M GL:86.320 MWL:94.820
SR @ karanthaneri (S)
L:100M GL:88.425
MWL:96.925
SR(P) @ karanthaneri (M)
L:30M GL:88.720
MWL:96.720
SR @ Thalaikulam Nadar Qts
GL:95.815 MWL:103.815
SR @ Nedungulam Maravar Colony &
Nedungulam H
L:330M GL:93.550 MWL:102.050
SR(P)@ Nedungulam
Nadar colony
GL:90.370 MWL: 98.370
10
10
60
30
15
30
10
SR @ karanthaneri (N)
GL:93.235 MWL:101.235
10
30
10
10
30
LS:30 m
GL:68.800
LS:2760
GL:82.540
LS:3780
GL:82.910
LS:6000
GL:86.870
LS:6360
GL:86.600
LS:2340
GL:93.855
LS:570
GL:94.370
LS:2100 m
LS:7260 m
GL:86.320
LS:7950 m
GL:89.370
LS:8670 m
GL:88.425
LS:9240 m
GL:88.720
LS:9960 m
LS:2370 m
GL:93.340
LS:3270 m
LS:30 m
GL:93.685
LS:0 m
LS:0 m
LS:0 m
250
500
LS:330 m
12/ 13
13/ 15
14/ 15
15/ 17
29/ 32
42/ 47
54/ 60
13/ 14
67/ 74
12/ 13
14/ 15
10 / 10
36/ 38
10/ 10
14/ 16
24/ 26
60/ 64
127/ 138
160/ 174
33/ 36
10/ 10
17/ 19
177/ 193
187/ 203
187/ 203
Branch to SR @ Poolam
0 m to 900 m : 50 mm PVC 6 Ksc [Proposed]
Branch to SR @ Panankulam
0 m to 30 m : 63 PVC 4 Ksc [Existing]
Branch ti SR @ Mudalaikulam Maravar Colony
0 m to 140 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Mudalaikulam Nadar colony
0 m to 75 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Karanthaneri South
0 m to 100 m : 63 PVC 4 Ksc [Proposed]
Branch to Prop. SR @ Karanthaneri Middile
0 m to 30 m : 63 PVC 4 Ksc [Proposed]
Branch to.SR @ Thalaikulam Nadar Qts
0 m to 2340 m :75 PVC 4 Ksc [Proposed]
2340 m to2370 m : 63 PVC 4 Ksc [Existing]
2370 m to 3270 m : 63 PVC 4 Ksc [Proposed]
Branch to SR @ Thalaikulam Reddiyar Qts
0 m to 30 m : 63 PVC 4 Ksc [Existing]
Branch to Prop.SR @ Nedungulam Nadar colony
0 m to1770 m : 63 PVC 4 Ksc [Existing]
1770 m to 2100 m : 50 PVC 6 Ksc [Proposed]
Branch to Nedunkulam Maravar Colony
0m to 330 m :50 PVC 6 Ksc [Proposed]
Pump set:
5 HP Subt x 187 lpm x 57 m [Proposed]
Pumping main:
Sump @ Singikulam to SR @ Karanthaneri [N]
0 to 2760 m : 110 PVC 6 Ksc [Proposed]
2760 m to 6000 m : 110 PVC 4 Ksc [proposed]
6000 m to 6360 m : 90 PVC 4 Ksc [Proposed]
6360 m to 7260 m :63 PVC 4 Ksc [Proposed]
7260 m to 9240 m :63 PVC 4 Ksc [Existing]
9240 m to 9960m :63 PVC 4 Ksc [Proposed]
Branch to SR @ Chinnapudukulam H
0 m to 1500 m : 50 PVC 6 Ksc [Proposed]
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District
Details
No. Habitations : 13
No. of Panchayat : 3
No. of Service Reservoirs: 12
[ Existing – 10 Proposed – 2]
Sump @ Singikulam to SR @ Karanthaneri (N)
FM 0 m to 1200 m
FM 1590 m to 2880 m
SR @ Chinnapudukulam H
L:1500M GL:86.225 MWL:94.225
24/25

## Slide 13
GROUP - 4
Pumping main from Sump @ marukalkuruchi to Meenavankulam
10
Ex. Sump cum Pump roomm &
Prop. Sump @ Marukalkuruchii
LWL:99.885 GL: 100.885
MWL:101.885
SR @ Meenavankulam
GL:97.405 MWL:107.975
30
LS:0 m
LS:60 m
GL:101.005
10
LS:2655m
GL:102.665
60
LS:4895 m
LS:450
GL:102.630
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District
SR @ Srivaramangaipuram
L:15 M GL: 102.645
MWL:110.645
Pump set:
1 HP Subt x 99 lpm x 22 m [Proposed]
Pumping main:
Sump @ Marukalkuruchi to SR @ Meenavankulam
0 to 60 m : 75 PVC 4 Ksc [Proposed]
60 m to 4645 m : 63 PVC 4 Ksc [Existing]
4645 m to4895 m : 50 GI [Existing]
Branch to SR @ Srivaramangaipuram
0 m to 15 m : 63 PVC 4 Ksc [Existing]
Branch to Prop SR @ Vilvarayankulam
0 m to 3660 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Marukalkurichi
0 m to 5 m : 63 PVC 4 Ksc [Existing]
33/ 36
12/ 13
45/ 49
99/ 107
Details
No. Habitations : 4
No. of Panchayat : 2
No. of Service Reservoirs: 4
[ Existing – 3 Proposed – 1]
SR @ Marukalkuruchi
L:5M GL:98.450 MWL:108.950
SR (P)@ Vilvarayankulam H
GL:94.880MWL:102.880
FM 0 m to 1850 m
60
10
LS:1810 m
GL:98.265
10/ 10
54/ 58
44/ 48
LS:0
LS:3660 m

## Slide 14
GROUP - 5
Pumping main from Sump @ Marukalkuruchi to Perumpathu
10
Sump cum Pump roomm @ Marukalkuruchii
LWL:99.885 GL: 100.885
MWL:101.885
SR @ Perumalthoppu &
Sankarnagar
L:300 M GL:101.665 MWL:110.165
FM 0 m to 2100 m
SR @ Manjankulam
L:675M GL: 94.015
MWL:102.015
.SR(P) @ Veerankulam
GL:93.305 MWL:101.305
30
LS:52 m
GL:101.005
LS:1777 m
GL:102.850
LS:2047 m
GL:102.960
30
LS:2362 m
GL:102.260
60
SR @ Perumpathu
GL:95.750 MWL:106.25
LS:3712
GL:96.670
30
SR @ Arasankulam - Krishnanpudur
L:2100 M GL:85.595
MWL:94.095
LS:420 m
GL:94.365
LS:885 m
GL:91.685
10
10
LS:2460 m
LS:0 m
17/ 19
19/ 21
36/ 40
59/ 65
23/ 25
42/ 46
10 / 11
10 / 10
20/ 21
136/148
156/169
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District
Pump set:
3 HP Cent x 190 lpm x18m [Existing]
Pumping main:
Sump @ Marukalkuruchi to SR @ Perumpathu
0 to 1777 m : 90 PVC 4 Ksc [Existing]
1777 m to 2362 m : 90 PVC 4 Ksc [Proposed]
2362 m to 3818 m : 63 PVC 4 Ksc [Existing]
Branch to Prop.SR @.Nambi Nagarr
0 m to 180 m : 63 PVC 4 Ksc [Proposed]
Branch to SR @ Abdulkasim Nagar
0 m to 100 m : 63 PVC 4 Ksc [Existing]
Branch to Prop. SR @ Elanthoppu
0 m to 300 m : 63 PVC 4 Ksc [Proposed]
Br. To SR @ Perumalthoppu &Sankarnagar
0 m to 300 m :63 PVC 4 Ksc [Proposed]
Br to SR @ Arasankulam Krishnanpudur
0 m to 2100 m : 63 PVC 4 Ksc [Existing]
Br to SR @ Manjankulam
0m to 675 m 63 PVC 4 Ksc[Existing]
Details
No. Habitations : 9
No. of Panchayat : 3
No. of Service Reservoirs: 8
[ Existing – 5 Proposed – 3]
10
15
30
LS:52 m
GL:101.005
SR @ Abdul Kasim Nagar
L:100 M GL:102.355
MWL:111.355
LS:1972 m
GL:102.705
10
SR (P)@ Elanthoppu
L:300 M GL:103.300
MWL:111.300
10
SR(P) @ Nambi nagar
L:180 M GL: 103.400
MWL:111.400
15/ 16
10/ 10
146/158
10/ 11
156/169
121/132
101/111
Br. To Prop. SR @ Veerankulam
0 m to 2235 m :63 PVC 4 Ksc [Existing]
2235 m to 3810 m :63 PVC 4 Ksc [Proposed]
LS:3818

## Slide 15
GROUP - 6
Details
No. Habitations : 7
No. of Panchayat : 3
No. of Service Reservoirs: 5
[ Existing – 4, Proposed – 1]
10
Booster Station @ Perumalnagar
Ex.Sump cum Pump room & Prop. Sump
GL : 75.550 m
LWL: 75.150 m
MWL: 77.150 m
SR @ Keelakarankadu, Nadukarankadu, Melakarankadu
L: 10M GL:83.790 MWL:92.290
SR(P)@ Keelakarankadu H
GL: 84.625 MWL:92.625
10
SR @ Perumalnagar
L:100 M GL: 78.225
MWL:86.225
10
SR @ Thattankulam
GL: 83.515 MWL:91.515
LS:600 m
GL:78.225
10
10
LS:1765 m
GL:83.935
LS:1815 m
GL:84.180
30
LS:565 m
GL:77.985
LS:1420 m
LS:1245 m
LS:30 m
GL:76.045
LS:4315 m
LS:0
FM 1815 m to 4315 m
LS:0
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District
60
79/ 82
62/ 63
52/ 53
40/ 40
10/ 10
30/ 30
10/ 10
17/ 19
12/ 13
Pump set:
3HP cent x 80lpm x 26 m [Existing]
Pumping main:
Sump @ Perumalnagar to Prop. SR @ Keelakarankadu [H]
0 to 1815 m : 63 PVC 4 Ksc [Existing]
1815 m to 4315 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Keelakarankadu
0 m to 10 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Eraippuvari
0 m to 1420 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Perumalnagar
0 m to 100 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Thattankulam
0 m to 1245 m : 63 PVC 4 Ksc [Proposed]
FLOW DIAGRAM
Sump @ Perumal Nagar to SR @ Keelakarankadu [H]
SR @ Eraippuvari
GL :80.210 MWL:88.210
78/ 80

## Slide 16
10
SR @ Meenachinathapuram
L:15M GL:69.770 MWL:77.770
.
SR(P) @ Veppankulam
L:100M GL:68.235
MWL:76.235
SR(P) @ Muthalapuram
L:50M GL:67.535 MWL:75.535
SR @ Pattarpuram(1)
L:10M GL:79.070
MWL:87.570
SR @ Sebasthiyarpuram
GL:67.420 MWL:75.420
SR @ Thoranakuruchi
GL:82.625 MWL:91.125
30
LS:265 m
GL: 76.720
30
30
SR @ Pattarpuram(2)
L:40M GL: 81.655
MWL:90.155
10
LS:2925 m
GL:79.070
LS:3630
GL:81.655
LS:1650 m
GL: 69.770
LS:1800 m
GL:69.395
10
10
10
LS:2250 m
GL:67.535
LS:2160 m
GL:72.945
LS:0
LS:4700 m
LS:30 m
GL:76.045
LS:2430m
GROUP - 7
Details
No. Habitations : 6
No. of Panchayat : 3
No. of Service Reservoirs: 7
[ Existing – 5, Proposed – 2]
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District
Pump set:
2 HP cent x 85 lpm x 35 m [Proposed]
Pumping main:
Sump @ Perumalnagar to SR @ Thoranakuruchi
0 to 30 m : 63 PVC 4 Ksc [Existing]
30 m to 265 m : 63 PVC 4 Ksc [Proposed]
265 m to 2925 m : 63 PVC 4 Ksc [Existing]
2925 m to 4700 m : 63 PVC 4 Ksc [Proposed]
Branch to SR @ Sebesthiyarpuram
0 m to 2430 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Meenachinathapuram
0 m to 15 m : 63 PVC 4 Ksc [Existing]
Branch to Prop.SR @ Veppankulam
0 m to 100 m : 50 PVC 6 Ksc [Proposed]
Branch to Prop.SR @ Muthalapuram
0 m to 50 m : 50 PVC 6 Ksc [Proposed]
Branch main to SR @ Pattarpuram [2]
0 m to 40 m : 63 PVC 4 Ksc [Proposed]
FLOW DIAGRAM
Sump @ Perumal Nagar to SR @ Thoranakuruchi
Booster Station @ Perumalnagar
Ex.Sump cum Pump room & Prop. Sump
GL : 75.550 m
LWL: 75.150 m
MWL: 77.150 m
60
85/ 90
48/ 50
12/ 13
36/ 37
20/ 20
10/ 10
10/ 10
17/ 18
37/ 40
20/ 22
37/ 40
16/ 17
85/ 90

## Slide 17
10
Sahayanagar Colony
L:220M GL:74.955
MWL:83.455
SR @ Emankulam
Pudukulam Colony H
L:360MGL:73.690
MWL:82.190
SR(P) @ South Kariyakulam
GL:65.155 MWL:73.155
SR @ Subramaiyapuram
L:20M GL:69.390
MWL:79.890
SR(P)@ Kariyakulam
L:100M GL:68.435
MWL:76.435
SR @ Kanmaniyankudiyiruppu
L:70M GL:72.065 MWL:80.565
SR(P)@ Parpanathapuram H
GL:64.830 MWL:72.830
30
LS:580
GL:76.385
LS:930
GL: 75.760
30
60
LS:3840
GL:70.235
LS:3990
GL:69.390
10
10
LS:4200
GL: 68.435
LS:5865 m
GL:72.065
30
30
LS:4215 m
GL: 68.445
10
LS:585 m
GL:65.660
10
LS:4635 m
GL:70.270
10
LS:6345 m
LS:855 m
LS:30 m
GL:76.045
10
Booster Station @ Perumalnagar
Ex.Sump cum Pump room & Prop. Sump
GL : 75.550 m
LWL: 75.150 m
MWL: 77.150 m
60
GROUP - 8
Details
No. Habitations : 12
No. of Panchayat : 3
No. of Service Reservoirs: 11
[ Existing – 7, Proposed – 4]
Pump set:
2 HP Sub. x 186 lpm x 24 m [Proposed]
Pumping main:
Sump @ Perumalnagar to SR @ Alangulam
0 to 580 m : 110 PVC 4 Ksc [Proposed]
580 m to 3840 m : 90 PVC 4 Ksc [Proposed]
3840 m to 3990 m : 63 PVC 4 Ksc [Existing]
3990 m to 4715 m : 63 PVC 4 Ksc [Proposed]
4715 m to 5715 m : 63 PVC 4 Ksc [Existing]
5715 m to 6345 m : 63 PVC 4 Ksc [Proposed]
Branch to SR @ Korkaneri
0 m to 820 m : 50 PVC 6 Ksc [Proposed]
820 m to 830 m : 63 PVC 4 Ksc [Existing]
Branch to Prop. SR @ South Kariyakulam
0 m to 3810 m : 63 PVC 4 Ksc [Existing]
3810 m to 5190 m : 50 PVC 6 Ksc [Proposed]
Branch to.SR @ Emankulam pudukulam H
0 m to 360 m : 63 PVC 4 Ksc [Existing]
FLOW DIAGRAM
Sump @ Perumal Nagar to SR @ Alangulam
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District
SR @ Korkaneri
GL:74.020
MWL:82.020
10
LS:830 m
LS:235 m
GL: 76.720
18/ 19
28/ 31
19/ 21
47/ 52
SR (P)@ Paul Nagar& Indira nNagar
L:70M GL:65.660 MWL:73.660
SR @ Subramaniapuram
L:40M GL:70.270 MWL:78.270
SR @ Alangulam
GL:71.880
MWL:80.380
11/ 12
58/ 64
30/ 30
LS 0
20/ 20
10/ 10
88/ 94
15/ 16
103/ 110
24/ 26
14/ 15
186/ 199
14/ 15
28/ 30
14/ 15
13/ 14
41/ 44
127/ 136
LS 0
LS 550
LS 900
FM4715 m to 5715 m
127/ 136
LS:5190 m
Branch to SR @ Sahayanagar colony
0 m to 220 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Subramaniyapuram
0 m to 20 m : 63 PVC 4 Ksc [Existing]
Branch to Prop. SR @ Kariyakulam
0 m to 100 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Parpanathapuram H
0 m to 855 m : 50 PVC 6 Ksc [Proposed]
Branch to Prop. SR @ Paul Nagar
0 m to 70 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Subramaniyapuram [Elangulam]
0 m to 40 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Kanmaniyankudiyiruppu
0 m to 70 m : 63 PVC 4 Ksc [Proposed]

## Slide 18
GROUP - 9
Details
No. Habitations : 13
No. of Panchayat : 5
No. of Service Reservoirs: 14
[ Existing – 10, Proposed –4]
Pumping main from Sump @ Mavadi to SR @ Achiyoor colony
10
LS:1350 m
GL:70.680
SR @ Thulukkarpatti(1)
L: 20M GL:70.895
MWL:81.395
SR @ Anaiikulam
L:20 M GL:68.380
MWL:76.880
SR @ Mavadi
L:10 M GL: 70.680
MWL:78.680
60
60
SR @ Thulukkarpatti(2)
L:540 m GL: 70.385
MWL:80.885
30
SR @ Eraniankudiyiruppu
L: 10M GL:71.975
MWL:80.475
10
SR (P) @ Mylapudhur(E)
L : 20m GL:72.810 MWL:80.810
10
LS:1815
GL:71.170
LS:1845 m
GL:71.220
LS:285 m
GL:70.940
SR (P) @ Thalaivanmanai
L:30M GL:70.940
MWL:78.940
30
30
SR @ Vaithiyalingapuram
GL: 65.410 MWL:73.910
LS:4965 m
30
SR @ Mylapudhur(W)
L : 810m GL :75.680
MWL:84.180
LS:2325
GL:71.875
LS:2385 m
GL:71.905
LS:3225 m
GL:68.645
LS:3345 m
GL:68.380
10
SR (P) @ Anaiikulam(h)
L:570M GL:65.815
MWL:73.815
150
100
223/ 239
213/ 228
10/ 11
48/ 52
102/ 110
10/ 10
92/ 100
10/ 11
14/ 16
165/ 176
63/ 66
10/ 10
53/ 56
10/ 10
43/ 46
12/ 13
31/ 33
LS:0 m
P’ set: 3 HP cent x 30 lpm x 38 m [Existing]
Pumping main:
Sump @ Mavadi to SR @ Veppilankulam West
0 to 1350 m : 110 PVC 4 Ksc [Existing]
1350 m to1815 m : 100 CI LA Cl [Existing]
1815 m to 1845 m : 110 PVC 4 Ksc [Existing]
1845 m to 2325 m : 63 PVC 4 Ksc [Existing]
2325 m to 4645 m : 63 PVC 4 Ksc [Proposed]
4645 m to 6185 m :63 PVC 4 Ksc [Existing]
6185 m to 6515 m :63 PVC 4 Ksc [Proposed]
Branch to SR @ Mavadi
0 m to10 m : 50 GI [Existing]
Branch to SR @ Thulukkapatti SR [2]
0 m to 540 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Thulukkapatti SR [1]
0 m to 20 m : 50 GI [Existing]
Branch to SR @ Vaithiyalingapuram
0 m to 3225 m : 110 PVC 4 Ksc [Existing]
3225 m to 4845m : 63 PVC 4 Ksc [Existing]
4845 m to 4965 m : 63 PVC 4Ksc [Proposed]
Branch to Prop.SR @ Thalaivanmanai
0 m to 30 m : 50 PVC 6 Ksc [Proposed]
Branch to Prop.SR @ Anaikulam H
0 m to 570 m : 50 PVC 6 Ksc [Proposed]
Branch main to SR @ Anaikulam
0 m to 20 m : 63 PVC 4 Ksc [Existing]
Branch to SR @Mylapudur West
0 m to 600 m : 63 PVC 4 Ksc [Existing]
600 m to 810 m : 63 PVC 4 Ksc [Proposed]
Branch to SR @ Eranian Kudiyiruppu SR
0 m to 10 m : 50 PVC 6 Ksc [Proposed]
Branch to Prop. SR @ Mylapudur East
0 m to 20 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Achiyoor
0 m to 30 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Karunkannankudiyiruppu
0 m to 30 m : 63 PVC 4 Ksc [Existing]
30 m to 210 m : 63 PVC 4Ksc [Proposed]
Branch to SR @ Chinnammalpuram
0 m to 450 m :50 PVC 6 Ksc [Proposed]
Branch to Prop.SR @ Veppilankulam East
0 m to 30 m : 63 PVC 4Ksc [Proposed]
Branch to.SR @ Veppilankulam West
0 m to 600 m : 63 PVC 4Ksc [Existing]
600 m to 930 m : 63 PVC 4Ksc [Proposed]
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai
TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District
LS:0 m
10
SR @ Karunkannan
kudiyiruppu
GL: 75.310MWL:83.310
LS: 30 m
GL: 75.310
10
SR @ Veppilankulam (W)
GL:76.845
MWL:84.845
SR (P)@ Veppilankulam(E)
L: 30M GL:73.280
MWL:81.280
LS: 5585 m
GL:75.155
LS:5135 m
GL:73.280
30
SR @Achiyoor(H)
GL: 74.035
MWL:82.535
30
30
SR @Chinnammalpuram
L: 450 m GL: 72.450
MWL: 80.950
LS: 4865 m
GL:73.460
LS:550 m
GL:74.145
LS:990 m
10
SR @Achiyoor
L:30M GL:73.965
MWL:82.465
13/ 14
13/ 14
42/ 45
31/ 33
11/ 12
21/ 23
10/ 10
10/ 11
11/ 12
FM 600 m
26/ 28
LS: 4645
GL:72.960
LS: 210 m
LS:2745 m
GL:72. 810
LS:0 m
68/ 73
78/ 84
Sump @ Mavadi
E P
LWL:75.415 75.915
GL:77.415 77.415
MWL:78.915 78.915
LS: 6515 m
Br to SR @ Achiyyor (H)
0 m to 550 m :63 PVC 4 Ksc [Existing]
550 m to 990 m :63 PVC 4 Ksc [Proposed]

## Slide 19
GROUP - 10
Details
No. Habitations : 6
No. of Panchayat : 2
No. of Service Reservoirs: 6
[ Existing – 5, Proposed – 1]
Pumping main from Sump @ Shunmugapuram to SR @ Nallammalpuram
SR @ Shanmugapuram
L:1395M GL:80.310
MWL:89.310
10
Sump @ Shanmugaouram
GL: 86.205 LWL: 84.600
MWL: 86.600
LS: 15 m
GL:86.320
15
LS: 370 m
GL:86.780
30
SR @ Kandiaperi(H)
L:65 M GL:86.780
MWL:95.280
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District
10/ 10
13/ 14
86/ 92
Pump set:
3 HP Sub x 125 lpm x 25 m [Existing]
Pumping main:
Sump @ Shunmhgapuram to SR @ Nallammalpuram
0 m to4710 m : 90 PVC 4 Ksc [Existing]
4710 m to 4720 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Kandigaiperi H
0 m to 65 m : 63 PVC 4 Ksc [Proposed]
Branch to SR @ Shunmugapuram
0 m to 1395 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Melapandarapuram
0 m to 15 m : 63 PVC 4 Ksc [Existing]
Branch to Prop.SR @ Keelapandarapuram
0 m to 30 m : 63 PVC 4 Ksc [Proposed]
Branch to SR @ Kandiaperi
0 m to 480 m : 63 PVC 4 Ksc [Proposed]
SR @ Melapandarapuram
L: 15M GL:88.675
MWL: 97.175
LS:1230 m
GL: 88.675
30
10
SR (P) @ Keelapandarapuram
L:30M GL: 87.705
MWL:95.705
LS:1520 m
GL:87.705
30
LS:4710 m
GL: 88.395
SR @ Nallankulam
GL: 88.395
MWL:96.895
30
SR @ Kandiaperi
L:480M GL : 86.895
MWL: 95.395
10/ 10
53/ 58
14/ 15
39/ 43
19/ 21
76/ 82
63/ 68
LS:4720 m
10

## Slide 20
30
SR @ Moolakadu
GL: 70. 930
MWL:79.430
GROUP - 11
Details
No. Habitations : 5
No. of Panchayat : 2
No. of Service Reservoirs: 4
[ Existing – 4, Proposed – 0]
Pumping main from Sump @ Moolaikadu to SR @ Theraikulam
SR @ Vandalampadu
L:15M GL: 69.775 MWL:77.775
SR @ Teraikulam H & Teraikulam Yadav
GL:64.375 MWL:72.375
5
Booster Station Moolakadu
Existing Sump
GL:69.745 LWL: 68.455
MWL: 71.455
LS:60 m
GL: 70. 930
TO RADHAPURAM SUMP
LS:540 m
GL: 69.775
LS:1920 m
30
10
SR @ Muthunadar kudiyiruppu
GL: 64.430 MWL:72.930
10
10/ 11
12 / 13
11/ 12
14 / 15
21/ 23
26/ 28
10/ 10
13/ 13
20/ 20
25 /25
30/ 30
38 / 38
51/ 53
64 / 66
LS: 30 m
70.785
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District
Pump set:
1 HP Sub x 60 lpm x 40 m [Existing]
Pumping main:
Sump @ Moolakadu to SR @ Moolakadu
0 m to90 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Theraikulam H
0 m to 1920 m : 63 PVC 6 Ksc [Existing]
Branch to SR @ Muthunadarkudiyiruppu
0 m to 300 m : 63 PVC 4 Ksc [Proposed]
300 m to 1300 m : 63 PVC 4 Ksc [Existing]
1300 m to 1350 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Vandalampadu
0 m to 15 m : 63 PVC 4 Ksc [Existing]
LS:90 m
LS:0 m
LS:1350 m
LS:0 m
FM LS 300 m to 1300 m

## Slide 21
GROUP - 12
10
Sump cum Pumproom & Prop. Sump
@ Samugarengapuram
GL: 50.280 LWL: 48.780 MWL: 51.780
SR @ Ponnathi H & Pudukuruchi
L:240MGL:27.180MWL:35.680
SR @ Kasthurirengapuram
L:25MGL: 27.525
MWL:38.025
SR @ Mudavankulam
L:20MGL: 26.000
MWL:34.500
SR @ Aymudi
L:1530MGL:30.190
MWL:38.190
SR @ Perunkannankulam
L:120MGL:26.535
MWL:35.035
15
SR @ Anaikarai(2)
L:40MGL: 26.240MWL:35.240
SR @ Kutti Nainarkulam
L:1000MGL:24.775
MWL:33.275
SR (P) @ Kailasapaei
GL:20.400
MWL:28.400
10
SR(P) @ Pulikulam H
GL:27.330MWL:35.330
60
30
30
30
10
10
30
30
SR @ Anaikarai(1)
L:20MGL: 23.635MWL:32.135
LS:240
GL: 50.440
LS:1860
GL: 50.635
LS:2250
GL:49.045
LS:5220
GL:43.185
LS:5730
GL:41.005
LS:10230
GL:27.525
LS:10470
GL:26.845
LS:11580
GL:26.505
LS:12750
GL:26.130
LS:15480
GL:26.400
LS:240 m
GL:26.095
LS:0
LS:2130 m
GL:26.000
LS:5310 m
LS:15330
GL:23.635
LS:15840
LS:30
GL: 51.270
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District
200
Details
No. Habitations : 12
No. of Panchayat : 4
No. of Service Reservoirs: 12
[ Existing – 10, Proposed – 2]
Pumping main from Sump @ Samugarengapuram to Prop. SR @ Pulikulam H
10/ 10
50/ 55
60/ 65
60/ 65
16/ 18
76/ 83
10/ 10
86/ 93
10/ 10
17/ 19
27/ 29
16/ 18
43/ 47
129/ 140
49/54
20/ 20
30
100
LS:420 m
GL: 51.305
SR @ Samugarengapuram
GL: 51.300 MWL:61.300
LS:440 m
LS:0 m
SR @ Kattaneri
L:960 M GL: 54.690
MWL:63.190
198/214
139/ 152
16/ 17
155/ 169
353/ 383
Pump set:
7.5 HP Sub x 353 lpm x 35 m [Proposed]
Pumping main:
Sump @ Samugarengapuram to SR @ Pulikulam H
0 m to 30 m : 110 PVC 6 Ksc [Proposed]
30 m to 5220 m : 110 PVC 4 Ksc [Existing]
5220 m to 10230 m : 110PVC 6 Ksc [Proposed]
10230 to 15480 m : 63 PVC 4 Ksc [Existing]
15480 m to 15840 m : 63 PVC 4 Ksc [Proposed]
Branch to SR @ Samugarengapuram
0 m to 440 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Kattaneri
0 m to 600 m : 63 PVC 4 Ksc [Existing]
600m to 960m : 50 PVC 6 Ksc [Proposed]
Branch to SR Ponnathi & Pudukurichi H
0 m to 240 m : 50 PVC 6 Ksc [Proposed]
Branch to Kasthurirengapuram
0 m to 25 m : 63 PVC 4 Ksc [Existing]
Branch to Prop. SR @ Kailasaperi
0 m to 2130 m : 63 PVC 4 Ksc [Existing]
2130 m to 5130 m : 63 PVC 4 Ksc [Existing]
5130 m to 5310 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Kuttinainarkulam
0 m to 700 m : 63 PVC 4 Ksc [Existing]
700 m to 1000 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Mudavankulam
0 m to 20 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Aymedu
0 m to 1530 m : 63 PVC 4 ksc [Existing]
Branch to SR @ Perunkannankulam
0 m to 120 : 63 PVC 4 Ksc [Existing]
Branch to SR @ Anaikari 2
0 m to 40 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Anaikarai 1
0 m to 20 m : 63 PVC 4 Ksc [Proposed]
FM 2130 m to 5130 m
FM 0 m to 700 m
LS:0 m
198/214

## Slide 22
10
Ex.Sump cum Pumproom &
Prop Sump @ Samugarengapuram
GL: 50.280 LWL: 48.780 MWL: 51.780
60
SR @ Seelathikulam
GL:44.255
MWL:54.755
SR @ Seelathikulam
Colony L:990M
GL:43.605
MWL:52.105
SR @ Vaiagaoundapatty(2)
GL: 43.815 MWL:51.815
SR @ Kumbikulam(S) & Naduvur H
GL: 44.110MWL:52.610
SR @ Kannankulam
L:20MGL: 35.205
MWL:44.205
SR @ Kottaikarungulam
L:20MGL: 39.730
MWL:50.230
SR @ Vadivammanpatti
L:555 MGL: 39.185
MWL:49.685
10
SR (P) @ Vadaseri
GL:34.190
MWL:42.190
SR @ Vaiagaoundapatty(1)
L:15M GL:43.780
MWL:52.280
SR @ Kumbikulam Casba
L:20mGL:50.635
MWL:59.135
30
SR @ Durai Kudiyiruppu(E)(Nadar)
L:435M GL:57.000 MWL:65.500
30
SR @ Durai Kudiyiruppu (W)( Yadav)
GL:59.995 MWL:68.495
SR @ Therkku AD Colony
L:20M GL:49.950
MWL:58.450
30
30
30
10
30
30
15
60
60
L180 m
LS:240 m
GL: 50.440
LS:1620 m
GL: 50.635
LS:2010 m
GL:49.045
LS:4980 m
GL:43.185
LS:5490 m
GL:41.005
LS:1080 m
GL: 44.110
LS:2490 m
GL:35.205
LS:5880 m
GL:39.615
LS:3510 m
GL: 44.350
LS:450 m
GL: 49.950
LS:3630 m
GL: 44.255
LS:1400 m
GL: 43.780
LS:30 m
GL: 51.270
LS:2760
LS:2010 m
GL: 58.710
GROUP - 13
Details
No. Habitations : 13
No. of Panchayat : 5
No. of Service Reservoirs: 13
[ Existing – 12, Proposed – 1]
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District
Pumping main from Sump @ Samugarengapuram to SR @ Seelathikulam
52/ 57
55/ 60
107/ 117
10/ 10
10/ 10
10/ 10
20/ 20
127/137
20/ 20
10/ 10
10/ 10
147/ 157
10/ 10
157/167
16/ 18
16/ 18
63/69
79/87
19/ 21
98/108
15/ 16
110/ 122
267/ 289
17/ 19
18/ 19
35/ 38
302/ 327
200
LS 0
LS 3650 m
Pump set:
5 HP sub x 350 lpm x 40 m [Existing]
Pumping main:
Sump @ Samugarengapuram to SR @ Seelathikulam
0 m to 240 m : 110 PVC 4 Ksc [Proposed]
240 m to 810 m : 90 PVC 4 Ksc [Existing]
810 m to 1810 m : 80 CI LA [Existing]
1810 m to 3650 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Kottaikaungulam
0 m to 5490 m : 90 PVC 4 Ksc [Proposed]
5490 m to 5900 m ; 90 PVC 4 Ksc [Existing]
Branch to SR @ Duraikudiyiruppu West
0 m to 2760 m : 63 PVC 4 Ksc [Existing]
Branch to SR Duraikudiyiruppu East
0 m to 435 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Kumbikulam Kasba
0 m to 20 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Kumbikulam south & Naduvur H
0 m to 1090 m : 63 PVC 4 Ksc [Existing]
Branch to Prop.SR @ Vadaseri
0 m to 2490 m : 63 PVC 4 Ksc [Existing]
2490 m to 3750 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Kannankulam
0 m to 20 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Vadivammanpatti
0 m to 555 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Therkku AD Colony
0 m to 20 m : 50 PVC 6 ksc [Proposed]
Branch to SR @ Seelathikulam Colony
0 m to 990 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Vaiagoundampatti 1
0 m to 1415m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Vaiagounampatti 2
0 m to 180 m : 63 PVC 4 Ksc [Existing]
LS 0 m
LS 5900 m
LS 0 m
L:3750M
LS:1090M
LS:0M

## Slide 23
GROUP -14
Details
No. Habitations : 5
No. of Panchayat : 3
No. of Service Reservoirs: 7
[ Existing – 7, Proposed – 0]
Pumping main from Sump @ Samugarengapuram to SR(2) @ A.Thirumalapuram
10
Ex. Sump cum Pump room &
Proposed Sump @ Samugarengapuram
GL: 50.280 LWL:48.780 MWL:51.780
Enan Kudiyiruppu
L:350M GL: 54.440
MWL:62.440
Singarathoppu
L:20M GL: 54.220
MWL:62.720
Ottakarankudiyiruppu
L:60M GL: 64.985
MWL:72.985
A.Thirumalapuram(2)
GL: 71.000 MWL:81.500
30
30
60
Soundarapndiapuram(2)
L:20M GL:62.705 MWL:73.205
Soundarapndiapuram(3)
L:500M GL:64.835 MWL:73.335
10
30
60
A.Thirumalapuram(1)
L:125M GL:69.840
MWL:78.340
10
LS:750
GL:54.330
LS:2460
GL:54.220
LS:4920
GL:62.255
LS:5010
GL:62. 705
LS:6810 m
GL:64.985
LS:8940 m
126/137
116/126
61/66
31/ 33
12/13
55/60
10/11
136/147
10/10
PUMP SET:
3 HP cent x 150 lpm x38m [Existing ]
PUMPING MAIN:
Sump @ Samugarengapuram to SR @ A.Thirumalapuram 2
0 m to150 m :125 GI Medium [ Proposed]
150 m to 560 m : 110 PVC 4 Ksc [Existing]
560 m to 900 m : 100 CI LA [Existing]
900 m to 5010 m : 110 PVC 4 Ksc [Existing]
5010 m to 8940 m : 90 PVC 4 Ksc [Existing]
Branch to SR @ Enankudiyiruppu
0 m to 350 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Singarathoppu
0 m to20 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Soundrapandiapuram(2)
0 m to20 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Soundrapandiapuram(3)
0 m to500 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Othakarankudiyiruppu
0 m to 60 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ A.Thrumalapuram(1)
0 m to 125 m : 50 PVC 6 Ksc [Proposed]
LS:0
49/53
18/ 20
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District
200
LS:8400 m
GL:69.540
LS:150
GL:52.240

## Slide 24
GROUP - 15
Details
No. Habitations : 12
No. of Panchayat : 3
No. of Service Reservoirs: 14
[ Existing – 12, Proposed – 2]
Pumping main from Sump @ Radhapuram to SR @ Subramaniaperi
Ex.Sump & Prop. Sump
@ Radhapuram
LWL:45.475GL: 47.475
MWL:48.475
30
SR @ Kariyakulam
L:30M GL:47.390 MWL:55.890
SR @ Radhapuram(3)
GL:43.070 MWL:53.070
SR @ Mahendram
L:20M GL:41.800
MWL:50.300
SR @ Pavirithottam
L:130M GL:46.965
MWL:56.465
SR @ Pappankulam
GL: 48.245 MWL:56.745
10
SR [P] @ Pavendar
Barathidasan Nagar
L:630MGL:47.760
MWL:55.760
SR @ Valkadambu
L:135M GL: 57.615
MWL:65.615
SR[P] @ Vallarkulam
L:280M GL:44.090 MWL:52.090
100
SR @ Radhapuram(1)
GL: 47.475 MWL:57.475
10
SR @ Semmankulam
GL: 55.390 MWL:63.390
10
SR @ Subramaniyaperi
GL: 59.325 MWL:67.325
10
30
30
10
30
30
LS:60
GL:47.190
LS:870
GL:44.600
LS:1050
GL:44. 990
LS:1590
GL:47.195
LS:4240
GL:57.580
LS:4990
GL:59.455
LS:6430
60
SR @ Radhapuram(2)
L:60M GL: 43.830 MWL:54.330
LS:240 m
GL:44.010
LS:450 m
GL:43.985
SR @ Pannaiyarkulam
L:840M GL:44.000
MWL:52.500
30
SR @ Nakkaneri
GL:37.240
MWL:45.740
LS:90
GL:43.830
LS:480
LS:0
LS:1440 m
GL:41.800
LS:6540
LS:0
LS:750
GL:46.425
LS:0 m
LS:330
GL:47.340
LS:4370
LS:2040
302/328
277/302
217/239
158/174
59/65
60/63
50/53
30/33
15/16
15/17
20/20
10/10
10/10
25/26
10/10
15/16
PUMP SET:10HP Sub 302pm x 32m [Proposed]
PUMPING MAIN: (To Subramaniaperi)
0 m to 870 m : 110 PVC 4 Ksc [Existing]
870 m to 1590 m : 63 PVC 6 Ksc [Existing]
1590 m to 5990 m : 63 PVC 4 Ksc [Existing]
5990 m to 6430 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Pavendhar Bharathidasan nagar
0 m to 630 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Pappankulam
0 m to 2040 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Pavirithottam
0 m to130 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Valkadambu
0 m to135 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Semponkulam
0 m to 4370 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Kariakulam
0 m to30 m : 63 PVC 4 Ksc [Existing]
Branch to SR (2) & (3) @ Radhapuram
480+60=540 m : 63 PVC 4 Ksc [Proposed]
Branch to SR @ Nakkaneri
0 m to 900 m : 110 PVC 4 Ksc [Existing]
900 to 6540 :63 PVC 4Ksc [Proposed]
34/38
15/17
19/21
15/17
10/10
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District
100
100
400
Branch to SR @ Mahendram
0 to 20 m : 63 PVC 4 Ksc [Existing]
Branch toSR @ Pannaiyarkulam
0 m to840 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Vallarkulam
0 m to280 m : 50 PVC 6 Ksc [Proposed]
FM 4990 m to 5990 m
10/10

## Slide 25
GROUP - 16
Details
No. Habitations : 5
No. of Panchayat : 2
No. of Service Reservoirs: 5
[ Existing – 5, Proposed – 0]
Pumping main from Sump @ Radhapuram SR @ Kattalaicheri
100
SR @ Athukuruchi
GL: 25.740 MWL:36.240
SR @ Chidambarapuram
L:250M GL:25.895 MWL:36.395
SR @ Kattalaicheri
GL: 34.490 MWL:42.990
SR @ Udhayathoor
Yadhavar kudiyiruppu
L:10M GL:24.695
30
LS:5670
GL:33.535
60
30
60
SR @ Prakasapuram
L:10M GL: 26.535
MWL:35.035
LS:3750
GL:26.535
LS:4650
LS:3000
GL:27.270
LS:6870
10
LS:270
GL:32.500
SR @Ilaiyanainarkulam
L:50M GL: 31.845 MWL:39.845
Sump @ Radhapuram
LWL:45.475 GL: 47.475
MWL:48.475
125/138
15/17
110/121
15/16
95/105
53/59
38/42
15/17
PUMP SET: 1 HP sub x 125 lpm x 5m [Proposed ]
PUMPING MAIN:
Sump @ Radhapuram to SR @ Kattalaicheri
0 m to 1320 m : 90 PVC 4 Ksc [Proposed]
1500 m to 5670 m : 140 PVC 4 Ksc [Existing]
5670 m to 6870 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Athukurichi
0 m to 3000 m : 140 PVC 4 Ksc [Existing]
3000 m to 4650 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Ilaiya nainarkulam
0 m to 50 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Chidambarapuram
0 m to 250 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Prakasapuram
0 m to 10 m : 63 PVC 4 Ksc [Existing]
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District
42/46
LS:1500 m
GL:43.570
400
LS:1320 m
GL:43.990
LS:0

## Slide 26
GROUP - 17
Details
No. Habitations : 11
No. of Panchayat : 3
No. of Service Reservoirs: 13
[ Existing – 11, Proposed – 2]
Pumping main from Sump @ Radhapuram to SR @ Udayathur yadavar Kudiyiruppu
100
Ex.Sump & Prop.
@ Radhapuram
LWL:45.475 GL: 47.475
MWL:48.475
SR @ Vaniankulam
GL: 30.135 MWL:38.135
SR @ Parameswarapuram (1)
L:90M GL:37.715MWL:48.215
SR @ Battarkulam
L:840M GL:40.955
MWL:48.955
60
10
30
SR @ Parameswarapuram (3)
L:60M GL:38.365MWL:46.865
30
Sr @ selvavinayagarpuram
GL:41.450 MWL:49.950
10
SR @ Kakkan nagar
L:470M GL:39.655
MWL:47.655
LS:4515
GL:38.545
LS:4350
GL:37.715
LS:3000
GL:38.510
LS:90
GL:38.370
10
30
LS:5115
GL:36.200
LS:5955
GL:32.300
SR @ Vilaketri nainarkulam
L: 45M GL:32.300 MWL:40.800
10
SR [P] @ Udhaya rajapuram
L: 350M GL:28.300 MWL:36.300
30
60
SR @ Udhayathoor(1)
L:10M GL:27.470 MWL:35.970
SR @ Udhayathoor(2)
L:70M GL:27.345 MWL: 37.845
LS:7485
GL:27.470
30
SR @ Udhayathoor
Yadhavar kudiyiruppu
GL:24.695 MWL:33.195
LS:9135
GL:24.695
10
SR [P] @ Erumbucheri
L: 390 M GL:23.315
MWL : 31.315
10
SR @Vattavilai
L:315M GL:25.785
MWL:33.785
LS:1785
LS:7305
GL:29.085
LS:7515
GL:27.905
LS:8295
GL:27.440
202/216
192/206
192/206
107/114
97/104
84/90
74/80
26/28
10/10
16/18
10/10
38/42
10/10
13/14
10/10
17/19
58/63
75/82
10/10
LS:540
PUMP SET: 2 HP Sub x 202 lpm x 15m [Proposed ]
PUMPING MAIN:
Sump @ Radhapuram To SR @ Udayathur Yadavar Kudi
0 m to 1500 m : 150 AC Cl 10 [Existing]
1500 m to 4515 m : 140 PVC 4 Ksc [Existing]
4515 m to 5115 m : 110 PVC 4 Ksc [Existing]
5115 m to7515 m : 63 PVC 4 Ksc [Existing]
7515 m to 9145 m : 50 PVC6 Ksc [Proposed]
Branch to SR @ Battarkulam
0 m to 840 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Kakkan nagar
0 m to 470 m : 50 PVC 6 Ksc [Proposed]
Branch to SR (3) @ Parameswarapuram
0 m to150 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Selva Vinayagarpuram
0 m to 540 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Vaniyankulam
0 m to1275 m : 63 PVC 4 Ksc [Existing]
1275 m to1785m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Vilaketri Nainarkulam
0 m to45 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Udhayarajapuram
0 m to 350 m : 50 PVC 6 Ksc [Proposed]
Branch to SR (1) & (2) @ Uhayathoor
0 m to10 m : 63PVC 4 Ksc [Existing]
0 m to 70 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Vattavilai
0 to 315 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Erumbucheri
0 m to 390 m : 50 PVC 6 Ksc [Proposed]
LS:1275
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side
Habitations including Kalakadu TP in Tirunelveli District
36/38
74/ 80
400
10/10
LS:9145 m

## Slide 27
SR @ Thanakkarkulam
L:1800M GL: 52.475
MWL:62.975
SR @ Manikkampudur
L:1260MGL: 54.450
MWL:62.450
SR @ Betherngapuram
GL: 61.015 MWL:71.515
GROUP - 18
Details
No. Habitations : 6
No. of Panchayat : 2
No. of Service Reservoirs: 6
[ Existing – 6, Proposed – 0]
Pumping mainfrom Vadakkankulam Sump to SR @ Betherengapuram
SR @ Kalkarai
L:2060M GL:58.715
MWL:67.215
LS:1020 m
GL: 61.535
LS:1770 m
GL: 60.680
LS:2040
GL: 58.990
SR @ Kalkarai Colony
GL:57.305 MWL:65.805
LS:480
LS:0
LS:2000 m
GL: 61.015
LS:1560
GL: 54.385
SR @ Ramachandra nagar
L:10M GL: 54.385
MWL:62.385
Ex.Sump & Prop. Sump @ Vadakkankulam
GL: 55.410 LWL:54.410
MWL:56.910
LS:2070
LS:0
129/137
119/127
10/10
77/84
32/36
45/48
10/10
35/38
42/43
32/33
10/10
PUMP SET: 2 HP Sub x 129 lpm x 25 m [PROPOSED ]
PUMPING MAIN:
Sump @ Vadakkankulam To SR @ Betharengapuram
0 m to 2070 m : 90 PVC 4 Ksc [Existing]
Branch to SR @ Manickampudur
0 m to 1260 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Thanakkarkulam
0 m to1800 m : 90 PVC 4 Ksc [Existing]
Sub Branch to SR @ Ramachandranagar
0 m to10 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Kalkarai
0 m to 2060 m : 90 PVC 4 Ksc [Existing]
Sub Branch to SR @ Kalkarai colony
0 m to 480 m : 50 PVC 6 Ksc [Proposed]
50
300
60
10
60
30
10
30
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District

## Slide 28
GROUP -19
Details
No. Habitations : 5
No. of Panchayat : 2
No. of Service Reservoirs: 5
[ Existing – 5, Proposed – 0]
10
Krishnapuram
L:1270MGL: 61.065
MWL:69.065
LS:5565
GL :63.010
Puthiyamputhur
L:15M GL: 58.310
MWL:66.810
50
30
LS:5970
GL :58.310
LS:6360
GL :54.540
30
30
Soundralingapuram
GL: 50.790 MWL:59.290
LS:450 m
GL :52.610
LS:3180
GL :58.340
Ex. Sump Prop. Sump
@ Vadakkankulam
GL: 55.410 LWL: 54.410
MWL:56.910
Madanadarkudyiruppu
GL: 58.725 MWL:67.225
30
30
Shanmugapuram
L:10mGL: 52.610
MWL:61.110
94/97
10/10
2121
73/76
11/11
18/19
44/46
62/65
104/107
PUMP SET:3HP Sub x 125 lpm x 25 m [Existing]
PUMPING MAIN:
Sump @ Vadakkankulam to SR @ Mada nadar kudiyiruppu)
0 m to 5970 m : 90 PVC 4 Ksc [Proposed]
5970 m to 6360 m : 75 PVC 4 Ksc [Proposed]
6360 m to 6960 m : 63 PVC 4 Ksc [Existing]
6960 m to 7170 m : 63 PVC 4 Ksc [Proposed]
Branch to SR @ Soundralingapuram
0 m to 750 m : 63 PVC 4 Ksc [Proposed]
750 m to 770 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Shanmugapuram
0 m to 10 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Krishnapuram
0 m to 1270 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Puthiyamputhoor
0 m to 15 m : 63 PVC 4 Ksc [Existing]
LS:7170
LS:770 m
LS:0
300
LS:750 m
GL :50.790
LS:6960 m
GL :57.205
Pumping main from Sump @ Vadakkankulam to SR @ Madanadarkudiyiruppu
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District

## Slide 29
50
GROUP - 20
Details
No. Habitations : 11
No. of Panchayat : 2
No. of Service Reservoirs: 11
[ Existing – 11, Proposed – 0]
PUMPING MAIN FROM SUMP @ VADAKKANKULAM TO SR @ KAVALKINARU VILAKKU
30
SR @ Perungudi Colony
L:80MGL: 65.610MWL:74.110
30
SR @ Perungudi
L:15MGL:66.055MWL:74.555
30
SR @ South Veppilankulam
L. 2760 M GL:69.970 MWL78.470
SR @ Perunkaliyapuram
L:10MGL:73.840MWL:82.340
100
SR @ Lebbaikudiyiruppu
GL: 76.735 MWL:86.735
SR @ Kavalkinaru Zone I &
Kamaraj Nagar
L:600 M GL: 81.705 MWL: 92.205
SR @ Kavalkinaru Zone II
L: 240 m GL:80.660MWL:91.160
30
60
30
SR @ Ganapathiyapuram & Kakkan nagar
GL:81.155 MWL:89.655
10
SR @ Kavalkinaru Vilakku
GL: 96.880MWL:104.880
60
30
SR @ Ambedhkar nagar
L:60MGL: 78.140MWL86.640
60
SR @ Kavalkinaru
Zone III
L:540MGL:82.585MWL:93.085
LS:3490
GL:66.130
LS:3990
GL: 64.440
LS:4320
GL:66.055
LS:5860
GL:73.905
LS:6300
GL: 76.840
LS:6240
GL: 76.615
LS:6780
GL: 80.895
LS:8130
LS:90
GL: 76. 820
LS:240
GL: 79.725
LS:1570 m
LS:110
GL:78.650
Ex. Sump & Prop. Sump
@ Vadakkankulam
GL: 55.410 LWL: 54.410
MWL:56.910
197/199
19/19
178180
20/21
158/159
10/10
148/149
10/10
138/139
78/79
14/14
21/22
79/87
43/43
60/60
20/20
10/10
10/10
40/40
10/10
30/30
20/20 &
10/10
PUMP SET: 5 HP subx 197x 58m [Proposed ]
PUMPING MAIN: To SR @) Kavalkinaru vilakku
0 m to 1380 m : 150 CI A cl [Existing]
1380 m to 2130 m : 150 AC cl 15 [Existing]
2130 m to5860 m : 125 AC cl 15 [Existing]
5860 m to 6780 m : 125 AC cl 10 [Existing]
6780 m to 8130 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Perungudi colony
0 m to 80 m : 50 PVC 6 Ksc [Existing]
Branch to SR @ Veppilaankulam (S)
0 m to 2760 m : 50 PVC 6 Ksc [Existing]
Branch to SR @ Perungudi
0 m to 15 m : 50 PVC 6 Ksc [Existing]
Branch to SR @ Perunkaliapuram
0 m to 10 m : 50 PVC 6 Ksc [Existing]
Branch to SR @ Lebbaikudiyiruppu
0 m to 90 m : 90 PVC 4 Ksc [Proposed]
90 m to 600 m : 75 PVC 4 Ksc [Proposed]
600 m to 1570 m : 63 PVC 4 Ksc [Existing]
Branch to SR(2) @ Kavalkinaru
0 m to 240 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Ganapathiapuram
0 m to 540 m : 63 PVC 4 Ksc [Existing]
Branch to SR(3) @ Kavalkinaru
0 m to 650 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Ambedkarnagar
0 m to 60 m : 50 PVC 6 Ksc [Proposed]
Branch to SR (1) @ Kavalkinaru
0 m to 600 m : 90 PVC 4 Ksc [Existing]
Augmentation of Existing CWSS to
Nanguneri, Thisayanvilai TPs
and 297 way side Habitations
including Kalakadu TP in Tirunelveli District
LS:540 m
LS:600 m
75.755
LS:0 m
300

## Slide 30
GROUP -21
Details
No. Habitations : 6
No. of Panchayat : 2
No. of Service Reservoirs: 11
[ Existing – 11, Proposed – 0]
PUMPING MAIN FROM SUMP @ VADAKKANKULAM TO SR (2) @ VADAKKANKULAM
60
SR @ Sivasubramaniyapuram(1)
L; 10 M GL:48.060 MWL:58.560
10
SR @ Pallavilai(2)
GL:49.305MWL:57.305
60
SR @ Koliyankulam(1)
L:80M GL:41.845 MWL:52.345
60
LS:2130
GL:59.380
SR @ Vadakkankulam Zone III
L:530M GL:56.860 MWL:67.360
60
SR @ Sivasubramaniyapuram(2)
L : 600 m GL:47.510MWL:58.010
30
SR @ Pathinathapuram(1)
L:30M GL:44.160MWL:52.660
30
SR @ Pathinathapuram(2)
GL:44.125 MWL:52.625
10
SR @ Mariyasingapuram
L:190M GL: 51.695MWL:59.695
SR @ Koliyankulam(2)
GL: 46.960MWL:57.460
60
60
SR @ Vadakkankulam Zone II
GL:62.540MWL:73.040
100
SR @ Vadakkankulam Zone I
L:620M GL: 62.060MWL:72.060
LS:1380
GL: 57.320
LS:2400
LS:810
GL:54.395
LS:2880
GL:47.550
LS:3105
GL:48.060
LS:3750
GL:46.630
LS:4650
GL: 42.490
LS:5040
LS:3270
GL:44.160
LS:3300
Ex. Sump & Prop. Sump
@ Vadakkankulam
GL: 55.410 LWL: 54.410
MWL:56.910
203/208
29/30
10/10
25/27
19/20
57/59
44/46
92/92
20/20
52/52
20/20
PUMP SET: 3HP cent x 203 lpm x 30m Proposed]
PUMPING MAIN:
Sump @ Vadakkankulam to SR @ Vadakkankulam Z 2
0 m to 1380 m : 110 PVC 4 Ksc [Proposed]
1380 m to 2130 m : 63 PVC 4 Ksc [Proposed]
2130 m to 2400 m : 50 PVC 6 Ksc [Proposed]
Branch to SR(3) @ Vadakkankulam
0 m to 530 m : 63 PVC 4 Ksc [Proposed]
Branch to SR(1) @ Vadakkankulam
0 m to 620 m : 125 AC cl15 [Existing]
Branch to SR (2) @ pathinathapuram
0 m to 2880 m : 50 GI Medium [Existing]
2880 m to3300 m : 50 PVC 6 Ksc [Existing]
Branch to SR @ Mariasingapuram
0 m to 190 m : 50 PVC 6 Ksc [Proposed]
Branch to SR(1) @ Pathinathapuram
0 m to30 m : 50 PVC 6Ksc [Proposed]
Branch to SR(2) @ Koliyankulam
0 m to3105 m : 90 PVC 4 Ksc [Proposed]
3105 m to 5040 m : 50 PVC 6 Ksc [Existing]
Branch to SR(1) @ Siva subramaniapuram
0 m to 10 m : 50 PVC 6 Ksc [Existing]
Branch to SR(2) @ Siva subramaniapuram
0 m to 600 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Pallavilai
0 m to 1020 m : 50 PVC 6 Ksc [Existing]
LS:0
LS:0
82/86
13/ 13
50
300
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District
LS:1020 m
19/20

## Slide 31
GROUP - 22
Details
No. Habitations : 12
No. of Panchayat : 3
No. of Service Reservoirs: 13
[ Existing – 12, Proposed – 1]
Pumping main from Alaganeri Sump to Uralvoimozhi Colony
Prop. Sump @ Alaganeri
GL: 46.770 LWL: 45.270
MWL:48.270
30
10
10
30
10
Alaganerir
L:15M GL:46.770
MWL:55.270
AlaganerirColony
L:375MGL: 44.975
MWL:52.975
LS:50
GL :46.770
MelaSivasubramaniapuram
L:75M GL:47.805
MWL:56.305
Kilakulam(N)
L: 20M GL: 47.460
MWL:55.460
Kilakulam(W)
GL:46.920
MWL:54.920
LS:570
GL :44.150
10
Kilakulam(E)
L: 270MGL: 44.625
MWL:52.625
30
Adangarkulam
L:1230MGL:40.510
MWL:49.010
LS:1710
GL :40.140
LS:400
GL :49.265
LS:1780
GL :47.460
30
Sembikulam
L: 170M GL: 39.575
MWL:48.075
LS:1880
GL :39.000
30
Meenakshinathapuram
L: 250M GL: 38.900
MWL:47.400
LS:2070
GL :38.520
30
Mathaganeri(1)
L: 10M GL: 37.890
MWL:46.390
30
Mathaganeri(2)
L: 190M GL: 36.140
MWL:44.640
LS:2910
GL :38.295
LS:3120
GL :37.360
30
LS:6000
GL :32.150
Uralvoimozhi
L:210M GL:30.910
MWL:39.410
30
Uralvoimozhi Colony
GL:34.515 MWL:43.015
250/269
19/20
13/14
23/24
10/10
15/16
179/194
42/44
10/10
169/184
34/37
135/147
18/19
117/128
13/14
104/114
46/50
58/64
31/34
15/16
LS:7530
LS:2100
PUMP SET: 3 HPSub x 250 lpm x 26 m [Proposed ]
PUMPING MAIN: (To Uralvoimozhi colony)
0 m to 1880 m : 90 PVC 4 Ksc [Existing]
1880 m to 6000 m : 63 PVC 4 Ksc [Existing]
6000 m to 6200 m : 63 PVC 4 Ksc [Proposed]
6200 m to 7400 m : 63 PVC 4 Ksc [Existing]
7400 m to 7530m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Kilakulam (w)
0 m to 400 m : 63 PVC 4 Ksc [Proposed]
400 m to 1780 m : 63 PVC 4 Ksc [Existing]
1780 m to 2100 m : 63 PVC 4 Ksc [Proposed]
Branch to SR @ Mela sivasubramaniapuram
0 m to75 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Kilakulam (N)
0 m to20 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Alaganeri Colony
0 m to 375 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Alaganeri
0 m to 15 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Kilaulam (E)
0 m to270 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Sembikulam
0 m to 170 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Meenakshinathapuram
0 m to 250 m : 50 PVC 6 Ksc [Proposed]
Branch to SR (1) & (2) @ Mathaganeri
190 m : 63PVC 4 Ksc [Existing]
10 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Uralvoimozhi
0 m to 210 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Adankarkulam
0 m to1230 m : 63 PVC 4 Ksc [Existing]
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District
100
14/15

## Slide 32
Prop. Sump @ Alaganeri
GL: 46.770 LWL: 45.270
MWL:48.270
100
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District
Pazhavoor
GL: 46.945
MWL:56.945
100
60
KC Pazhavoor
L:350 M GL: 42.465
MWL:52.965
65/70
55/60
60
Pazhavoor(2)
L:100 M GL: 46.725
MWL:57.225
30/34
150/164
95/104
70/70
30/34
55/60
GROUP - 23
Details
No. Habitations : 2
No. of Panchayat : 1
No. of Service Reservoirs: 3
[ Existing – 3, Proposed – 0]
Pumping main from Alaganeri Sump to Palavoor
LS:7070
GL: 44.925
LS:7230
GL: 46.350
LS:7600
PUMP SET: 2 HPSub x 150 lpm x 25 m [Proposed ]
PUMPING MAIN: (To Palavoor)
0 m to 7070 m : 110 PVC 4 Ksc [Proposed]
7070 m to 7600 m : 63 PVC 4 Ksc [Proposed]
Branch to SR @ KC Palavoor
0 m to 350 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Palavoor 2
0 m to100 m : 50 PVC 6 Ksc [Proposed]

## Slide 33
GROUP - 24
Details
No. Habitations : 6
No. of Panchayat : 2
No. of Service Reservoirs: 6
[ Existing – 6, Proposed – 0]
Pumping mainfrom Sump @ Avaraikulam to SR @ Avaraikulam
AmbalavanapuramColony
L:390M GL: 55.225 MWL:63.725
15
Ex. Sump cum Pump room
@ Avaraikulam
GL:47.945 LWL: 46.445
MWL:48.445
LS:630
GL :51.205
100
Sivagnanapuram
L:885M GL: 49.095
MWL:59.095
60
Ambalavanapuram
L:10 M GL: 55.115
MWL:65.615
30
100
Avaraikulam
L:40MGL:52.120
MWL:62.120
222/242
14/16
46/50
114/125
10/10
170/185
PUMP SET:3 HP Sub x 350lpm x 40 m [ Existing]
PUMPING MAIN:
Sump @ Avaraikulam to SR @ Ambalavanapuram
0 m to 630 m : 140 PVC 4 Ksc [Existing]
630 m to 1290 m : 110 PVC 4 Ksc [Existing]
1290 m to 1300 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Sivagnanapuram
0 m to 885 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Avaraikulam
0 m to 40 m : 90 PVC 4 Ksc [Proposed]
Branch to SR @ Ambalavanapuram Colony
0 m to 390 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Pillaiyarkudiyiruppu
0 m to 3050 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Avaraikulam pudur
0 m to 1380 m : 50 PVC 6 Ksc [Proposed]
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District
Avaraikulam Pudur
L:1380M GL: 43.295
MWL:51.295
Pillaiyarkudiyiruppu
LS:3050M GL: 37.245
MWL:47.745
60
LS:3030
GL :37.105
10
LS:560
GL :45.475
10/10
28/31
LS:60
GL :47.820
184/201
LS:1290
GL :55.300
56/60
LS:780
GL :52.120
LS:2250
GL :38.235
38/41
60

## Slide 34
GROUP - 25
Details
No. Habitations : 5
No. of Panchayat :2
No. of Service Reservoirs: 6
[ Existing – 5, Proposed – 1]
Pumping main from Sump @ Avaraikulam to SR @ Chidambarapuram
60
Jacobpuram
GL: 31.675
MWL:41.675
LS:3090
GL :37.105
Marankulam(2)
GL: 27.070
MWL:35.570
60
LS:1300 m
GL :27.070
Chidambarapuram
GL: 34.615 MWL:45.115
Pro. Sump cum Pump room
near Avaraikulam
GL:45.760 LWL: 44.260
MWL:47.260
LS:4995
PUMP SET:5 HP sub x 218lpm x 31m [ Proposed]
PUMPING MAIN:
Sump @ Avaraikulam to SR @ Chidambarapuram
0 m to 60 m : 110 PVC 4 Ksc [Proposed]
60 m to 4995 m : 90 PVC 4 Ksc [Existing]
Branch to SR @ Avaraikulam pudur
0 m to 1380 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Pillaiyar kudiyiruppu
0 m to 2470 m : 50 PVC 6 Ksc [Proposed]
2470 m to 2490 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Jacobpuram
0 m to 150 m : 90 PVC 4 Ksc [Existing]
150 m to 240 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Marankulam(2)
0 m to 1300 m : 63 PVC 4 Ksc [Existing]
1300 m to 1400 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Marankulam(1)
0 m to 20 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ kothankulam
0 m to 1930 m : 75 PVC 4 Ksc [Existing]
1930 m to 2380 m : 63 PVC 4 Ksc [ Proposed]
2380 m to 4500 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Keelkulam
0 m to 1800 m : 63 PVC 4 Ksc [Existing]
30
10
Marankulam1
L:20M
GL: 27.070
MWL:35.070
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District
LS:1400 m
218/237
70/75
99/109
49/53
Keelkulam
LS:1800 M
GL : 28.775
MWL: 37.275
36/39
13/14
Kothanulam
LS:4500 M
GL : 20.165
MWL:29.165
100
60/65
10/10
30
15
LS:0 m
GL 34.620
LS:240 m
LS:0
218/237

## Slide 35
GROUP – 26
Details
No. Habitations : 7
No. of Panchayat : 2
No. of Service Reservoirs: 8
[ Existing – 5, Proposed – 3]
Pumping main from S.V.Narayanam Sump to SR @ Parapadi [2]
SR @ Thamaraikulam
[Kannanallur Pt]
L:50M GL:60.035
MWL:68.535
SR(P)@ Kalmanikkapuram
[Elangulam Pt]
L:20M GL:54.150 MWL:62.150
SR @ Veppankulam
L:30M GL:60.410
MWL:69.410
SR @ Parapadi(2)
GL:64.490
MWL:74.990
SR(P) @ Kalmanikkapuram
[Kannanallur Pt]
GL: 53.800 MWL:61.800
SR @(P) Thamaraikulam H
[Elangulam Pt]
GL:60.760 MWL:68.760
SR @ Thalavoipuram
L: 960 m GL:57.080 MWL:65.080
10
60
100
SR @ Parapadi(1)
L:10M GL:62.010
MWL:72.010
LS:3510
GL:63.010
15
10
LS:1650 m
GL:60.735
LS:1620 m
GL:60.685
LS:1260
GL:54.150
LS:1470 m
10
30
LS:2430 m
GL:60.035
10
LS:2520 m
LS:90 m
GL:62.010
LS:1770 m
GL:60.315
150
Ex. Sump & Prop. Sump @ S.V.Narayanam
GL: 52.530 m LWL: 50.030 , MWL: 53.030
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations including Kalakadu TP in irunelveli District
LS:4110 m
LS:0 m
LS:0
100
120/128
120/128
58/64
10/10
10/10
20/20
10/10
10/11
12/13
22/24
32/34
42/44
10/10
62/64
LS:2520 m
GL:58.970
PUMP SET: 3 HP Sub x 125lpm x 25m [ Existing]
PUMPING MAIN:
Sump @ S.V. Narayanam to SR @ Parapadi 2
0 m to 2520 m : 90 PVC 6 Ksc [Proposed]
2520 m to 3510 m : 63 PVC 4 Ksc [Existing]
3510 m to 4110 m : 63 PVC 4 Ksc [Proposed]
Branch to Prop. SR @ Thamaraikulam H
0 m to 2350 m : 63 PVC 4 Ksc [Existing]
2350 m to 2520 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Parapadi 1
0 m to 30 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Thalavoipuram
0 m to 960 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Veppankulam
0 m to 30 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Thamaraikulam
0 m to 50 m : 50 PVC 6 Ksc [Proposed]
Branch to Prop. SR @ Kalmanickapuram [Kann]
0 m to 1000 m : 63 PVC 4 Ksc [Existing]
100 m to 1470 m : 50 PVC 6 Ksc [Proposed]
Branch to Kalmanickapuram [Elan]
0 m to 20 m : 50 PVC 6 Ksc [Proposed]
LS:2350 m
GL:59.820

## Slide 36
GROUP – 27
Details
No. Habitations : 10
No. of Panchayat : 3
No. of Service Reservoirs: 9
[ Existing – 5, Proposed – 4]
Pumping main from S.V.Narayanam Sump to Savalaikarankulam
10
SR(P) @ Kakkannagar H
L:20M GL:55.985 MWL:63.985
10
SR @ Savalaikarankulam
GL:60.415 MWL:70.915
SR @ Periyanadar kudiyiruppu
L:10M GL:56.470 MWL:64.470
SR @ Sadayaneri
L:810M GL:60.345 MWL:68.845
SR(P) @ Kamarajnagar
L:150M GL:56.825
MWL:64.825
SR @ Bharathi Nagar
L:145M GL:58.125
MWL:66.625
SR(P) @ Vinayagapuram Colony
L:40M GL:60.135 MWL:68.135
SR @ Elangulam & Nedungulam
GL:58.970 MWL:67.470
60
10
SR [P] @ Kailasanathapuram
L: 1710 M GL:55.540 MWL:63.540
30
LS:2175 m
GL:57.700
10
LS:3000 m
GL:56.470
LS:4560 m
GL:60.415
LS:1140 m
GL:55.985
LS:450 m
GL:57.895
LS:1050 m
GL:56.155
30
LS:1170 m
GL:58.925
LS:1410 m
GL:59.595
30
LS:1470 m
GL:58.970
10
150
Ex. Sump & Prop. Sump @ S.V.Narayanam
GL: 52.530 m LWL: 50.030 , MWL: 53.030
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations including Kalakadu TP in irunelveli District
100
145/155
145/155
LS:4640 m
LS:1510 m
31/34
14/16
14/15
14/15
45/49
59/65
73/80
10/10
83/90
10/10
12/13
20/21
10/10
30/31
10/11
40/42
52/55
62/65
PUMP SET: 2 HP Sub x 145 lpm x 29 m [ proposed]
PUMPING MAIN:
Sump @ S.V. Narayanam to SR @ Savalaikarankulam
0 m to 4640 m : 90 PVC 4 Ksc [Existing]
Branch to SR @ Elangulam & Nedungulam
0 m to 1510 m : 63 PVC 4 Ksc [Existing]
Branch to Prop. SR @ Kailasanathapuram
0 m to 1710 m : 63 PVC 4 Ksc [Existing]
Branch to Prop. SR @ Kakkannagar H
0 m to20 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Periyanadarkudiyiruppu
0 m to 10 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Sadayaneri
0 m to 700 m : 63 PVC 4 Ksc [Existing]
700 m to 810 m : 50 PVC 6 Ksc [Proposed]
Branch to Prop. SR @ Kamarajnagar
0 m to 150 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Bharathinagar
0 m to 145 m : 50 PVC 6 Ksc [Proposed]
Branch to Prop. SR @ Vinayagarpuram
0 m to 40 m : 50 PVC 6 Ksc [Proposed]
LS:0 m

## Slide 37
100
SR @ North Vijayanarayanam
GL:50.015 MWL:60.015
10
SR [P] @ Raja Gopalapuram
GL:50.710 MWL:58.710
LS:4395 m
GL:50.015
30
LS:285
GL:49.970
30
SR @North Vijayanarayanam
for Kottaicheri
L:165M GL:48.450
MWL:56.950
SR(P)@Elaankal
L:600M GL:45.840
MWL:54.340
LS:2850
GL:51.310
30
SR @Inthakal
L:600M GL:47.850
MWL:55.850
10
SR @Thiruvadaneril
L:2160M GL: 38.415
MWL:46.415
30
SR @Andankulam
L:15M GL:45.425
MWL:53.925
10
30
SR (P)@Kumarancheri &
Periyammlputam
GL: 46.005 MWL:54.505
SR @Padapparkulam
L:2370 GL:44.270 MWL:52.770
LS:4050
GL:50.165
LS:690 m
GL:48.450
LS:1140 m
GL:47.015
LS:2190 m
GL:45.735
LS:2760 m
GL:45.220
LS:855 m
LS:2925 m
GL:46.125
LS: 3690 m
LS:3660 m
GL: 46.005
100
150
Sump @ S.Vijayanarayanam
LWL:50.030 GL: 52.530
MWL:53.030
Pumping main from S.V.Narayanam Sump to SR @ North Vijayanarayanam
LS:4410 m
LS: 0 m
251/275
251/275
16/17
16/18
32/35
100/110
132/145
21/23
13/15
34/38
14/15
48/53
13/14
61/67
21/24
82/91
19/20
101/111
233/256
18/19
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations including Kalakadu TP in irunelveli District
GROUP – 28
Details
No. Habitations : 10
No. of Panchayat : 1
No. of Service Reservoirs: 9
[ Existing – 6, Proposed – 3]
PUMP SET: 4 HP Sub x 251 lpm x 29 m [ proposed]
PUMPING MAIN:
Sump @ S.V. Narayanam to SR @ N.V.Narayanam
0 m to 4050 m : 110 PVC 4 Ksc [Proposed]
4050 m to 4410 m : 63 PVC 4 Ksc [Existing]
Branch to Prop. SR @ Kumarancheri
0 m to 690 m : 90 PVC 4 Ksc [Proposed]
690 m to 2190 m : 63 PVC 4 Ksc [Proposed]
2190 m to 2925 m : 63 PVC 4 Ksc [Existing]
2925 m to 3690 m : 63 PVC 4 Ksc [Proposed]
Branch to SR @ Inthankal
0 m to 600 m : 63 PVC 4 Ksc [Existing]
Branch to Prop. SR @ Rajagopalpuram
0 m to285 m : 63 PVC 4 Ksc [Existing]
285 m to 855 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Padapparkulam
0 m to 2000 m : 63 PVC 4 Ksc [Existing]
2000 m to 2370 m : 50 PVC 6 Ksc [Proposed]
Branch to Prop. SR @ Elangalcheri
0 m to 600 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Kottaicheri
0 m to 165 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Thiruvadaneri
0 m to 1800 m : 63 PVC 4 Ksc [Existing]
1800 m to 2160 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Andankulam
0 m to 15 m : 63 PVC 4 Ksc [Existing]

## Slide 38
GROUP - 29
Details
No. Habitations : 10
No. of Panchayat : 2
No. of Service Reservoirs: 11
[ Existing – 7, Proposed – 4]
Pumping main from South Vijayanarayanam Sump to SR @ S.V.Narayanam East
SR @ Nalanthula
GL:31.770 MWL:40.270
SR @ Nalanthula H
L:10M GL:35.105
MWL:43.105
SR @ Valaithottam(1)
GL:32.960
MWL:41.960
30
SR(P) @ Nadarkudiyiruppu
L:150M GL:31.735
MWL:40.235
SR @ Kumarapuram
L:40M GL: 31.570
MWL:40.070
SR [P] @ Kumarapuram H
L:50M GL:30.040
MWL:38.040
SR @ Tharagankadu
GL:27.585 MWL:36.085
SR(P)@ Rajiv Gandhi Nagar
L:1200M GL:35.660
MWL:43.660
30
SR(P)@ S.V. Narayanam (W)
L:20M GL: 51.445 MWL:59.945
Sump @ Thisayanvilaii
GL: 22.820 m
LS:1170
GL: 51.445
SR@ S.V. Narayanam (E)
GL: 51.445 MWL:59.945
LS:2130
GL:48.750
10
LS:6960 m
GL:37.310
10
30
LS:7710 m
GL:34.575
LS:7740 m
GL:34.315
15
30
SR @ Valaithottam(2)
L:190M GL:32.765
MWL:41.265
30
LS:8760 m
GL:32.500
30
LS:9120 m
GL:31.570
10
30
LS:9390 m
GL:30.040
LS:9840 m
GL:27.580
LS:10980 m
GL:26.460
LS:11430 m
LS:180
GL:32.765
LS:210
GL:35.105
LS:750
Sump @ S.Vijayanarayanam
GL: 52.530 m LWL: 50.030, MWL: 53.030
100
150
177/189
114/120
LS:2150 m
LS:0 m
LS:0 m
LS:240 m
LS:0 m
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District
18/19
45/50
10/10
19/20
26/29
10/10
19/21
10/10
10/10
20/20
46/49
65/70
10/10
20/20
84/90
104/110
159/170
PUMP SET: 2 HP Sub x 177 lpm x 16m [ proposed]
PUMPING MAIN:
Sump @ S.V. Narayanam to SR @ S.V.Narayanam East
0 m to 1170 m : 110 PVC 4 Ksc [Proposed]
1170 m to 2130 m : 90 PVC 4 Ksc [Proposed]
2130 m to 2150 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Tharagankadu
0 m to 6960 m : 90 PVC 4 Ksc [Proposed]
6960 m to 8760 m : 75 PVC 4 Ksc [Proposed]
8760 m to 9120 m : 63 PVC 4 Ksc [Proposed]
9120 m to 11430 : 50 PVC 6 Ksc [Proposed]
Branch to Prop. SR @ S.V.Narayanam West
0 m to 20 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Vazhaithottam 1
0 m to240 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Vazhaithottam 2
0 m to 190 m : 63 PVC 4 Ksc [Proposed]
Branch to Prop. SR @ Rajiv Gandhi Nagar
0 m to 1200 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Nalanthula
0 m to 210 m : 63 PVC 4 Ksc [Existing]
210 m to 750 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Nalanthula H
0 m to 10 m : 63 PVC 4 Ksc [Existing]
Branch to Prop. SR @ Nadarkudiyiruppu
0 m to 150 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Kumarapuram
0 m to 40 m : 63 PVC 4 Ksc [Existing]
Branch to Prop. SR @ Kumarapuram H
0 m to 50 m : 63 PVC 4 Ksc [Proposed]

## Slide 39
30
SR @Vijaya
Achambadu
L:100M GL:40.195
MWL:48.695
10
SR(P)@N.Achambadu
L:150M GL:40.570
MWL:48.570
10
SR @: :vadaliivilai
GL:43.840 MWL:51.840
10
SR @ kadayan kulam
L:580 M GL:42.350 MWL:50.350
10
SR @ Melapandara
kulam
L:170M GL:40.045
MWL:48.045
30
SR @Keelapandarakulam
L:10 M GL:38.775
MWL:47.275
30
SR @Perumpanai
L:180M GL:40.235
MWL:48.735
60
SR @Alagappapuram
GL:39.535 MWL:50.035
LS:3960
GL:40.750
LS:3430
GL:40.045
LS:2520
GL:40.095
LS:4100 m
GL:41.135
LS:4350 m
GL:41.265
LS:4980 m
GL:42.185
LS:1200
GL:39.745
LS:1600 m
GROUP – 30
Details
No. Habitations : 8
No. of Panchayat : 3
No. of Service Reservoirs: 8
[ Existing – 6, Proposed – 2]
Pumping main from Ittamozhi Sump to SR at Vadalivilai
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations including Kalakadu TP in irunelveli District
PUMP SET:4HP Sub x 200 lpm x 40 m [Existing]
PUMPING MAIN:
Sump @ Ittamozhi to SR @ VadalivilaI
0 m to 3430 m : 90 PVC 4 Ksc [Proposed]
3430 m to 3960 m : 63 PVC 4 Ksc [Proposed]
3960 m to 5580 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Kadayankulam
0 m to580 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Vijayaachampadu
0 m to 100 m : 63 PVC 4 Ksc [Existing]
Branch to Prop. SR @ North Achampadu
0 m to150 m : 63 PVC 4 Ksc [Proposed]
Branch to Prop. SR @ Melapandarakulam
0 m to 170 m : 63 PVC 4 Ksc [Proposed]
Branch to SR @ Alagappapuram
0 m to 1600 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Perumpanai
0 m to 180 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Keelapandarapuram
0 m to 10 m : 63 PVC 4 Ksc [Existing]
16/17
10/10
26/27
10/10
36/37
42/46
78/83
46/51
25/28
71/79
16/18
88/93
10/10
78/83
10
Ex. Sump cum Pump room &
Prop. Sump @ Ittamozhi
LWL:34.650 GL: 36.455
MWL:36.650
100
LS:2100
GL:38.775
175/190
175/190
159/172
LS:5580 m

## Slide 40
GROUP - 31
Pumping main from Ittamozhi Sump to SR @ Ittamozhi
10
SR @ Subramaniyapuram
L:165M GL:35.470 MWL:43.970
SR @ Vaganeri ( Sathan)
L:10M GL:35.590 MWL:44.590
LS:435 m
GL:37.265
LS:825
GL:36.415
30
LS:930
GL:36.540
15
LS:3290
10
SR @ Thottikaranvilai
L:15M GL:33.995 MWL:41.995
LS:1365
GL:35.590
Ex. Sump cum Pump room &
Prop. Sump @ Ittamozhi
LWL:34.650 GL: 36.455
MWL:36.650
100
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District
Details
No. Habitations : 6
No. of Panchayat : 2
No. of Service Reservoirs: 6
[ Existing – 5, Proposed –]
95/102
10/10
14/15
24/25
24/26
48/51
30
SR(P)@ Manakavalapuram
L:150M GL: 36.415 MWL:44.915
19/20
PUMP SET: 2 HP Sub x 167 lpm x 21 m [Proposed]
PUMPING MAIN:
Sump @ Ittamozhi to SR @ Ittamozhi
0 m to 435 m : 110 PVC 4 Ksc [Existing]
435 m to 1260 m : 90 PVC 4 Ksc [Existing]
Branch to SR @ Pudur
0 m to45 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Subramaniyapuram
0 m to165 m : 63 PVC 4 Ksc [Existing]
Branch to Prop. SR @ Manakavalapuram
0 m to 150 m : 63 PVC 4 Ksc [Proposed]
Branch to SR Thottikaranvilai
0 m to 3290 m : 63 PVC 4 Ksc [Existing]
SR @ Ittamozhi
GL:41.045 MWL:51.045
LS:1260
100
72/79
SR @ Pudur
L:45 M GL:35.915
MWL:44.415
30
LS:555 m
GL:36.310
167/181
167/181
67/71
28/31

## Slide 41
GROUP - 32
Details
No. Habitations : 8
No. of Panchayat : 2
No. of Service Reservoirs: 7
[ Existing – 5, Proposed – 2]
Pumping main from Pattarkattivilai Sump to SR Thuvarampadu
10
Ex.Sumpcum p’room &
Prop. Sump @ Pattarkattivilai
GL: 41.400 LWL : 40.045
MWL: 42.045
SR @ Malyankudiyiruppu(1)
GL:33.870 MWL:42.370
SR @ Mannarpuram
L:300M GL:37.500
MWL:46.000
SR @ Eranthai South &
Karithottam
L:50M GL:35.850
MWL:44.350
Rajagopalapuram
L:90M GL:34.720
MWL:42.720
SR(P)@ Eranthai(H)
GL:34.255 MWL:42.255
SR (U/P)@ Thuvarmpadu
GL: 36.390 MWL:44.390
SR (P)@ Velayuthapuram
L: 100 M GL: 35.430 m
MWL : 43.430
LS:10
GL:42.075
LS:510
GL:42.490
30
LS:3390 m
LS:150
GL:42.575
30
LS:2415
GL:37.290
LS:3190
GL:36.965
30
10
LS:3280
GL:36.550
LS:390
GL:34.850
10
10
10
LS:3825
GL:35.715
LS:4410
GL:35.630
LS:5670
LS:1860
GL:38.425
LS:840
LS:0
LS:0
116/122
17/18
60
99/104
33/36
66/68
20/21
10/11
10/10
46/47
10/10
16/17
26/27
20/20
10/10
10/10
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District
PUMP SET: 2 HP Sub x 125 lpm x 40m [ Existing]
PUMPING MAIN:
Sump @ Pattarkattivilai to SR @ Thuarampadu
0 m to 3280 m : 63 PVC 4 Ksc [Existing]
3280 m to 5670 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Malayadikudiyiruppu
0 m to3390 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Mannarpuram
0 m to 300 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Eranthai South
0 m to 50 m : 63 PVC 4 Ksc [Existing]
Branch to Prop. SR @ Eraranthai H
0 m to 390 m : 63 PVC 4 Ksc [Existing]
390 m to 840 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Rajagopalapuram
0 m to 90 m : 63 PVC 4 Ksc [Existing]
Branch to Prop. SR @ Velayuthapuram
0 m to 100 m : 50 PVC 6 Ksc [Proposed]

## Slide 42
GROUP - 33
Details
No. Habitations : 9
No. of Panchayat : 2
No. of Service Reservoirs: 8
[ Existing – 8, Proposed – 0]
Pumping main from Pattarkattivilai Sump to SR @ Sankanapuram H
10
10
SR @ Pattarkattivilai
GL:L:10M GL:42.040
MWL:50.040
SR @ Mittadar Kulam(1)
L:30M GL:33.280
MWL:43.780
SR @ Nambikuruchi
GL:32.905 MWL:41.405
SR @ Muthammalpuram
GL:39.015 MWL:47.515
SR @ Sevanthiyapuram &
Sevanthiyapuram H
L:150M GL:46.335
MWL:54.835
Sankanankulam H &
Sadagobanambipuram
GL:43.905 MWL:54.405
SR @ Sankanankulam
L : 1560 m GL:41.355 MWL:49.855
LS:10
GL:42.075
LS:510
GL:42.490
LS:600
GL:42.040
30
60
LS:150
GL:42.575
LS:2760 m
GL:46.190
30
LS:4620 m
LS:0
30
30
LS:2160 m
GL:35.750
LS:2280 m
GL:36.150
LS:2880 m
LS:0
LS:1320 m
LS:0
60
30
LS:1920 m
GL:33.280
SR @ Mittadar Kulam(2)
L : 180 M GL:33.280 MWL:41.780
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District
175/190
46/50
30/33
25/26
55/59
101/109
74/81
17/19
57/62
25/27
10/10
32/35
15/17
60
Ex.Sumpcum p’room &
Prop. Sump @ Pattarkattivilai
GL: 41.400 LWL : 40.045
MWL: 42.045
PUMP SET: 3 HP Sub x 175lpm x 27 m [ Proposed]
PUMPING MAIN:
Sump @ Pattarkattivilai to SR @ Sankanankulam H
0 m to 150 m : 75 PVC 4 Ksc [Proposed]
150 m to 2760 m : 63 PVC 4 Ksc [Existing]
2760 m to 4620 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Nambikuruchi
0 m to 510 m : 63 PVC 4 Ksc [Proposed]
510 m to 600 m : 63 PVC 4 Ksc [Existing]
600 m to 1500 m : 63 PVC 4 Ksc [Proposed]
1500 m to 2880 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Mittarkulam 1
0 m to 1950 m : 63 PVC 4 Ksc [Proposed]
Branch to SR @ Mittarkulam 1
0 m to 180 m : 63 PVC 4 Ksc [Proposed]
Branch to Prop. SR @ Pattarkattivilai
0 m to 10 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Muthaammalpuram
0 m to 1320 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Sankanankulam
0 m to 1560 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Seventhiyapuram
0 m to 150 m : 63 PVC 4 Ksc [Existing]
LS:1950 m
32/35

## Slide 43
GROUP - 34
Details
No. Habitations : 12
No. of Panchayat : 3
No. of Service Reservoirs: 12
[ Existing – 10, Proposed – 2]
Pumping main from Sump @ Pettaikulam to SR @ Thinaikarankulam
To Thisayanvilai
30
30
60
60
10
10
30
30
30
To Karaichithupudur
30
LS 830 m
GL: 26.205 m
SR @ Thinaikarankulam (E)
GL: 25.760 m, LWL : 31.760 m
MWL: 34.260 m.
LS 845 m
LS 470 m
GL: 25.000 m
SR @ Pettaikulam North (E)
L: 10 M GL: 25.120 m,
LWL : 31.120 m
MWL: 33.620 m.
Ex. Sump & Prop. Sump
@ Pettaikulam
GL : 24.675 m, LWL : 23.175 m
MWL: 25.175 m. 2.50 m dia
SR @ Pettaikulam (E)
L: 5 M GL: 24.505 m,
LWL : 30.505 m
MWL: 35.005 m.
LS 135 m
GL: 25.000 m
LS 5 m
GL: 24.675 m
LS 0 m
LS 215 m
GL: 24.765 m
LS 0 m
10
15
SR @ Perungulam (E)
GL: 21.380 m, LWL : 27.380 m
MWL: 29.380 m.
LS 1780 m
GL: 20.105 m
LS 0 m
LS 2035 m
GL: 21.180 m
LS 130 m
LS 2325 m
SR @ Perungulam (E)
GL: 20.405 m, LWL : 26.405 m
MWL: 29.405 m.
1
2
LS 645 m
GL: 26.735 m
SR @ Pettaikulam H (E)
L : 240 M GL: 25.315 m,
LWL : 31.315 m
MWL: 35.815 m.
LS 1490 m
GL: 27.330 m
SR @ Pasuvzhi (P)
L: 480 M GL: 27.525 m,
LWL : 33.525 m
MWL: 35.525 m.
LS 2075 m
GL: 25.775 m
SR @ Kailasapuram (P)
L: 235 M GL: 25.920 m,
LWL : 31.920 m
MWL: 33.920 m.
90 PVC
LS 2680 m
GL: 23.160 m
LS 3355 m
GL: 24.705 m
LS 3385 m
GL: 24.305 m
SR @ Mohamadiyan Ayankulam &
Maniyankudi (E)
L: 60 M GL: 23.730 m,
LWL : 29.730 m
MWL: 32.230 m.
LS 0 m
LS 1065 m
GL: 24.765 m
SR @ Thalaivanvilai (E)
GL: 23.255 m, LWL : 29.255 m
MWL: 31.755 m.
LS 1365 m
LS 5155 m
GL: 24.690 m
LS 5450 m
SR @ Chokkalingapuram (E)
GL: 23.395 m, LWL : 29.395 m
MWL: 31.895 m.
SR @ Ayankulam (E)
L: 85 M GL: 24.230 m,
LWL : 30.230 m
MWL: 32.730 m.
10
10/10
13/14
23/24
10/10
10/ 10
10/ 10
30/30
22/24
52/54
33/36
85/90
95/100
10/10
10/10
105/110
12/13
117/123
17/19
17/19
134/142
70/77
204/219
227/243
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District
60
PUMP SET:3 HP Sub x 250lpm x 40m [ Existing]
PUMPING MAIN:
Sump @ Pettaikulam to SR @ Chockalingapuram (E)
0 m to 2680 m : 140 PVC 4 Ksc [Existing]
2680 m to 5155 m : 110 PVC 4 Ksc [Existing]
5155 m to 5450 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Thinaikarankulam (E)
0 m to 470 m : 63 PVC 4 Ksc [Proposed]
470 m to 840 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Pettaikulam North
0 m to10 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Perungulam 2
0 m to 1780 m : 90 PVC 4 Ksc [Existing]
1780 m to 2035 m : 63 PVC 4 Ksc [Existing]
2035 m to 2325 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Perungulam 1
0 m to 130 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Pettaikulam
0 m to 5 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Pettaikulam H
0 m to 240 m : 90 PVC 4 Ksc [Existing]
Branch to Prop. SR @ Pazuvazhi
0 m to 480 m : 50 PVC 6 Ksc [Proposed]
Branch to Prop. SR @ Kailasapuram
0 m to 235 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Thalaivanvilai
0 m to 1365 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Ayankulam
0 to 85 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Mohamathiyan Ayankulam
0 m to 60 m : 63 PVC 4 Ksc [Existing]

## Slide 44
GROUP - 35
Details
No. Habitations : 4
No. of Panchayat : 2
No. of Service Reservoirs: 5
[ Existing – 4, Proposed – 1]
Pumping main from Sump @ Pettaikulam to SR @ Rammthapuram Thekkur
Ex. Sump & Prop. Sump
@ Pettaikulam
GL : 24.675 m, LWL : 23.175 m
MWL: 25.175 m. 2.50 m dia
LS 5 m
GL: 24.675 m
10
75/80
75/80
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District
60
LS 1995 m
GL: 20.105 m
To Thoppuvilai
1
2
10
15
LS 3655 m
GL: 19.530 m
0 m
LS 185 m
30
SR @ Ramthapuram Naduvur (E)
GL: 17.800 m, LWL : 23.800 m
MWL: 26.300 m.
LS 10 m
0 m
LS 4930 m
GL: 18.050 m
30
LS 5075 m
GL: 17.030 m
LS 120 m
10
SR @ Ramthapuram Thekkur (E)
GL: 17.070 m, LWL : 23.070 m
MWL: 25.570 m.
SR @ Ramthapuram Thekkur (E)
GL: 16.460 m, LWL : 22.460 m
MWL: 24.460 m.
0 m
LS 5345 m
LS 5340m
GL: 17.070 m
LS 2350 m
GL: 11.025 m
SR @ Andhrakudiyiruppu (P)
GL: 12.165 m, LWL : 18.165 m
MWL: 20.165 m.
LS 2475 m
SR @ Urumankulam (E)
GL: 19.080 m, LWL : 25.080 m
MWL: 28.080 m.
0 m
16/17
59/ 63
13/ 14
46/ 49
46/ 49
36/ 39
10/ 10
PUMP SET:1 HP Sub x 75 lpm x 18 m [ Proposed]
PUMPING MAIN:
Sump @ Pettaikulam to SR @ Ramthapuram Thekkur 2
0 m to 1995 m : 75 PVC 4 Ksc [Proposed]
1995 m to3655 m : 75 PVC 4 Ksc [Existing]
3655 m to 5340 m : 63 PVC 4 Ksc [Existing]
5340 m to 5345 m : 63 PVC 4 Ksc [Proposed]
Branch to SR @ Urumankulam
0 m to 185 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Ramthapuram Naduvur
0 m to 10 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Ramthapuram Thekkur 1
0 m to 120 m : 63 PVC 4 Ksc [Existing]
Branch to Prop. SR @ Andrakudiyiruppu
0 m to 2350 m : 63 PVC 4 Ksc [Existing]
2350 m to 2475 m : 50 PVC 6 Ksc [Proposed]

## Slide 45
GROUP - 36
Details
No. Habitations : 6
No. of Panchayat : 1
No. of Service Reservoirs: 4
[ Existing – 4, Proposed – 0]
Pumping main from Thisayanvilaii Sump to SR @ Thangammalpuram
30
30
30
30
SR @ Idachithattu & KarampaduE)
GL: 22.960 m, LWL : 28.960 m
MWL: 31.460 m.
Ex.Sump & Prop. Sump
@ Thisayanvilai
GL : 22.820 m,
LWL : 21.320 m
MWL: 23.820 m.
LS 0
LS 410 m
GL: 22.895 m
LS 1020 m
GL: 19.805 m
LS 1080 m
SR @ Appuvilai (E)
L : 400 m GL: 18.805 m, LWL : 24.805
MWL: 27.305 m.
LS 570 m
GL: 19.800 m
SR @ Sindhu Nagar & Lakhmi Nagar(E)
L : 40 m GL: 19.615 m, LWL : 25.615 m
MWL: 28.115 m.
SR @ Kamaraj Nagar(E)
L: 360 M GL: 20.230 m, LWL : 26.230 m
MWL: 28.730 m.
50
60
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District
33/34
68/71
LS 0 m
35/37
20/20
10/10
10/10
15/17
10/10
10/10
20/20
13/14
PUMP SET: 1 HP Sub x 68 lpm x 21 m [ Proposed]
PUMPING MAIN:
Sump @ Thisayanvilai to SR @ Kamarajnagar
0 m to 410 m : 150 AC cl 10 [Existing]
410 m to 980 m : 50 GI [Existing]
980 m to 1340 m : 50 PVC 6 Ksc [Proposed]
Branch to SR @ Sindhu Nagar
0 m to 40 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Appuvilai
0 m to 400 m : 50 PVC 6 Ksc [Existing]
Branch to SR @ Edachithattu
0 m to 1020 m : 150 AC cl10 [Existing]
1020 m to1080 m : 50 PVC 6 Ksc [Existing]
LS 1340 m

## Slide 46
GROUP - 37
Details
No. Habitations : 6
No. of Panchayat : 2
No. of Service Reservoirs: 6
[ Existing – 4, Proposed – 2]
Pumping main from Thisayanvilaii Sump to SR @ Suvishesapuram
Ex.Sump & Prop. Sump
@ Thisayanvilai
GL : 22.820 m,
LWL : 21.320 m
MWL: 23.820 m.
50
60
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District
113/120
PUMP SET: 3 HP Sub x 113 lpm x 41 m [ Proposed]
PUMPING MAIN:
Sump @ Thisayanvilai to SR @ Suvishesapuram
0 m to 1320 m : 90 PVC 6 Ksc [Proposed]
1320 m to 4220 m : 63 PVC 4 Ksc [Existing]
Branch to SR @ Mahadevankulam
0 m to 450 m : 63 PVC 4 Ksc [Existing]
Branch to Prop.SR @ Murambu
0 m to 1140 m : 63 PVC 4Ksc [Existing]
Branch to SR @ Anthoniyarpuram
0 m to 5 m : 63 PVC 4Ksc [Existing]
Branch to SR @ Nallammalpuram
0 m to 50m : 63 PVC 4Ksc [Proposed]
Branch to SR @ Ubaharamathakudiyiruppu
0 m to 1000m : 63 PVC 4Ksc [Proposed]
1000 m to1645 m : 63 PVC 4Ksc [Existing]
SR @ Ubakaramatha kudiyiruppu
L:1645M GL:34.340
MWL:42.340
SR @ Suviseshapuram
GL:33.980 MWL:44.480
SR @ Mahadevankulam
L:450 M GL: 27.050
MWL:37.550
SR(P) @ Murambu
GL:31.380 MWL:39.380
LS:4200
GL:33.550
60
10
30
Anthoniyarpuram
L:5M GL:31.550
MWL:40.050
10
60
LS:2580
GL:32.485
LS:190 m
GL:31.550
LS:1320
GL:28.810
LS:1140 m
82/86
10/10
10/10
10/10
30/30
52/56
42/46
10/10
10
LS:4220
10/10
Nallammalpuram
L:50M GL:31.550
MWL:39.550
31/34

## Slide 47
KALAKKADU WSIS FLOW DIAGRAM – PROPOSED SCHEME
3M
X
3M
SR [P] @ VADAMALAISAMUDRAM
GL : 112.000, LWL : 128.000
MWL : 130.500
Prop. SUMP AT KALAKADU
GL : 117.700, LWL : 116.200
MWL : 119.200
SR [P] @ MANJUVILAII
GL 124.860, LWL 140.860
MWL 143.360
SR @ SINGAMPATHU
GL 120.530, LWL 132.530
MWL 135.030
SR @ KOVILPATHU
GL 127.500, LWL 139.500
MWL 142.000
74 / 89
70 / 147
335 / 400
68 / 81
267 / 319
LS 1520
LS 2230
LS 290
LS 2830
LS 0
LS 2790
LS 2890
LS 125
LS 20
405 / 547
479 / 636
110 PVC 4 KSC
150 AC Cl 15
119.440
115.600
117.75
150
30
100
30
100
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District
PUMP SET: 7.5 HP Sub x 479 lpm x 34 m [ Proposed]
PUMPING MAIN:
Sump @ Kalakadu to SR @ Kovilpathu
0 m to 290 m : 160 PVC 4 Ksc [Proposed]
290 m to 1520 m : 150 AC cl15 [Existing]
1520 m to 2230 m : 140 PVC 4 Ksc [Existing]
2230 m to 2830 m : 110 PVC 4 Ksc [Existing]
Branch main to Prop SR @ Vadamalaisamudram
0 m to 2010 m : 63 PVC 4 Ksc [Proposed]
Branch to Prop.SR @ Manjuvilai
0 m to 2790 m : 150 AC cl15 [Existing]
2790 m to 2890 m : 75 PVC 4 Ksc [Proposed]
Branch to SR @ Singampathu
0 m to 125 m : 75 PVC 4 Ksc [Existing]
LS 0
LS 2010
LS 0

## Slide 48
SR [P] @ KALAKKADU
GL 128.930, LWL :144.930
MWL 148.530
SR @ KALAKKADU
GL 127.500, LWL 139.500
MWL 142.000
SR [P] @ CHIDAMBARAPURAM
GL 141.400, LWL 157.400
MWL 159.900
SR @ CHIDAMBARAPURAM
GL 141.200, LWL 153.200
MWL 155.700
SR [P] @ KAKKANNAGAR
GL 133.700
LWL 149.700
MWL 153.300
SR [P] @ MOONKILADI
GL 137.400, LWL 153.400
MWL 156.400
662 / 792
239 / 287
340 / 405
202 / 241
864 / 1033
53 / 64
186 / 223
320 / 382
103 / 123
423 / 505
LS 3440
LS 3760
LS 5120
LS 5150
LS 0
LS 615
LS 1110
LS1810
400M
LS 840
LS 0
LS 400
LS0
LS10
1204 / 1438
KALAKKADU WSIS FLOW DIAGRAM – PROPOSED SCHEME
LS 3060
GL128.680
GL128.960
GL131.320
3M
X
3M
150
Prop. SUMP AT KALAKADU
GL : 117.700, LWL : 116.200
MWL : 119.200
100
100
200
30
200
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District
60
PUMP SET: 30 HP Sub x 1204 lpm x 55 m [ Proposed]
PUMPING MAIN:
Sump @ Kalakadu to SR @ Chidambarapuram
0 m to 3760 m : 200 AC Cl 15 [Proposed]
3760 m to 5120 m : 160 PVC 4 Ksc [Proposed]
5120 m to 5150 m : 110 PVC 4 Ksc [Proposed]
Branch to SR @ Kalakadu
0 m to 400 m : 110 PVC 4 Ksc [Existing]
Branch to Prop.SR @ Kalakadu
0 m to 840 m : 110 PVC 4 Ksc [Proposed]
Branch to Prop. SR @ Moongiladi
0 m to 615 m : 140 PVC 4 Ksc [Proposed]
615 m to 1110 m : 110 PVC 4 Ksc [Proposed]
1110 m to 1810 m : 90 PVC 4 Ksc [Proposed]
Branch to Prop. SR @ Kakkannagar
0 m to 400 m : 110 PVC 4 Ksc [Proposed

## Slide 49
3.50
KALAKKADU WSIS FLOW DIAGRAM – EXISTING SCHEME (16 Hrs. PUMPING )
SR [P] @ MANJUVILAI
GL 124.860, LWL 140.860
MWL 143.360
116 / 143
255 / 224
LS 165
LS 30
LS2935
143 / 171
150 AC 15 CL
129.870
139.500
413 / 413
LS 150
125.465
124.600
110 PVC 4 KSC
LS 2920
SR [P] @ MELAPATHAI ( Abedkarnagar )
GL 139.500, LWL 151.500
MWL 154.500
158 / 189
INFILTRATION WELL
B.L 118.820
F.V.L 115.820
CONTROL ROOM
3M X 3M
150 AC 15 CL
LS 2505
90 PVC 4 KSC
143 / 171
100
60
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District
PUMP SET: 10 HP Sub x 413 lpm x 46 m [ Proposed]
PUMPING MAIN:
Sump @ Kalakadu to SR @ Melapathai
0 m to 165 m : 150 AC cl15 [Existing]
165 m to 2935 m : 110 PVC 4 Ksc [Proposed]
Branch to Prop. SR @ Manjuvilai
0 m to 30 m : 90 PVC 4 Ksc [Proposed]

## Slide 50
NANGUNERI WSIS FLOW DIAGRAM – PROPOSED SCHEME
30
NANGUNERI Ex.SUMP CUM PUMP HOUSE
GL 98.930M
LWL 97.430M
MWL 99.430M
168 / 206
THENNIMALAI Ex.SR
GL : 88.350M
LWL 100.350M
MWL 103.350M
LS 0
135
60
THERADI Ex.SR
GL : 95.820M
LWL 107.820M
MWL 110.320M
CHEKKADI Pro.SR
GL : 97.385M
LWL 109.385M
MWL 116.985M
483 / 594
LS 40
315 / 388
53 / 65
115 / 141
244 / 301
200 AC cl.15-40M
140PVC
110 PVC 4 ksc -1320M [P]
90 PVC 4 ksc -1689M
75 PVC 4 ksc -2359M
63 PVC 4ksc-163M
75 PVC 4 ksc -457M
63 PVC 4ksc-236 M
NANGUNERI Ex.SR
GL 99.430M
LWL 111.43M
MWL 114.43M
NANGUNERI PRO.SUMP
GL 98.930M
LWL 97.430M
MWL 99.430M
727 / 895
200
200
15
PUMP SET: 3 HP Cent x 340lpm x 21 m [ Existing]
PUMPING MAIN:
Sump @ Nanguneri to SR @ Nanguneri
0 m to 40 m : 200 AC cl15 [Existing]
PUMP SET: 7.5 HP Sub x 483 lpm x 27m [Proposed]
Sump @ Nanguneri to SR @ Thennimoolai
0 m to 40 m : 140 PVC 4 Ksc [Proposed]
40 m to 1729 m : 90 PVC 4 Ksc [ Existing]
1729 m to 4088 m : 75 PVC 4 Ksc [Existing]
4088 m to 4251 m : 63 PVC 4 Ksc [Existing]
Branch to Prop. SR @ Chekkadi
0 m to 1320 m : 110 PVC 4 Ksc [Proposed]
Branch to SR @ Theradi
0 m to 457 m : 75 PVC 4 Ksc [Existing]
457 m to 693 m : 63 PVC 4 Ksc [Existing]
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District

## Slide 51
50
60
200
500
60
60
SR @ Madathu Achampadu (E) Z2
GL: 23.350 m, LWL : 30.850
MWL: 33.850 m.
830/994
568/684
130/156
438/528
311/375
127/153
SR [P] @ Sathankulam Road Z3A & 3B
GL: 27.790 m, LWL : 39.790
MWL: 47.390 m.
SR @ Keeraikaranthattu (E) Z4
GL: 29.125 m, LWL : 36.625
MWL: 39.625 m.
SR @ Market (E) Z1A &1B
GL: 22.820 m, LWL : 34.820
MWL: 39.625 m.
LS 1330 m
GL: 26.430
LS 1450 m
LS 0 m
LS 60 m
23.130
LS 0 m
LS 1620 m
LS 1890 m
LS 0 m
Augmentation of Existing CWSS to Nanguneri, Thisayanvilai TPs and 297 way side Habitations
including Kalakadu TP in Tirunelveli District
Pumping main from Thisayanvilaii Sump to SRs @ Thisayanvilai TP
PUMP SET: 10 HP Subx 830 lpm x 23 m [Proposed]
12.5 HP cent x 560lpm x 42m [Existing]
PUMPING MAIN:
Sump @ Thisayanvilai to SR for Zone 1 @ Market
0 m to 30 m : 140 PVC 4 Ksc [Existing]
Sump @ Thisayanvilai to SR for Zone 3 @ Sathankulam Road
0 m to 60 m : 160 PVC 4 Ksc [Proposed]
60 m to 1450 m : 140 PVC 4 Ksc [Proposed]
Branch to SR for Zone 4 @ Keeraikaranthattu
0 m to 1620 m : 90 PVC 4 Ksc [Proposed]
Branch to SR for Zone 2 @ Madathu Achampadu
0 m to 1500 m : 110 PVC 4 Ksc [Proposed]
1500 m to 1890 m : 90 PVC 4 Ksc [Existing]
Ex.Sump & Prop. Sump
@ Thisayanvilai
GL : 22.820 m,
LWL : 21.320 m
MWL: 23.820 m.

## Slide 52
THANK YOU