THE SUGAR INDUSTRY LABOUR WELFARE FUND

BIDDING DOCUMENTS

for

Open National Bidding

for Works

Construction of New Community Wellness Centre at  Gokoola

Procurement Ref: SILWF OAB 6/2021-2022

Sugar Industry Labour Welfare Fund

15-21, Edith Cavell Street,

Port-Louis

Tel: 2122056

Fax:2089817

June 2022

TABLE OF CONTEXTS

|  |  | Page No. |
| --- | --- | --- |
| Section I | Instruction to Bidders | 1 |
| Section II | Bidding Forms | 8 |
|  | Bid Securing Declaration | 10 |
|  | Qualification Information | 11 |
|  | Bill of Quantities – 1 to 8 | 12-87 |
|  | Summary Sheet | 88 |
|  | Key Financial Information Form | 89 |
| Section III | Specifications |  |
|  | Statement of requirements /scope of work | 90 |
|  | Additional Specifications | 93 |
|  | Water Proofing System | 99 |
|  | Timber Specifications | 102 |
|  | Electrical, Fire Alarm and Air Condition, Scope of Work, Specifications and Performance requirements - Electrical and Allied Works - Electrical System - Fire Detection and Alarm System - Mechanical Ventilation and Air Conditioning System - … - Handing Over | 107 108 113 124 126 131 |
|  | Mechanical – Scope of Works and Specifications | 133 |
|  | Equipment Schedule | 149 |
|  | List of Drawings - Architectural, Structural, Electrical, Mechanical, site works | 154 |
| Section IV | General conditions of contract | 160 |
|  | Particular conditions of contract | 189 |
| Section V | Contract Forms |  |
|  | Performance Security Form | 195 |
|  | Advance Payment Security | 196 |
|  | Letter of Acceptance | 197 |
| Appendix I | Contact Agreement | 198 |
|  | Standard Specifications | 1-47 |

Section I: Instruction to Bidders

### 1.	Introduction

The Sugar Industry Labour Welfare Fund also referred as the Employer, invites eligible local contractors to submit their bid for the works described in detail hereunder. Any resulting contract shall be subject to the terms and conditions referred to in this document.

The project consists of the construction of a New Community Wellness Centre and other related works at Gokoola as described hereunder:

1.  Demolition works of existing part of boundary wall, kerbs,low wall and fencing,

steps, absorption pit, flower boxes as per drawings.

2.The construction of a new single storey Community Wellness Centre in reinforced    concrete structure, finished with the following works; - internal and external rendering/painting, ceramic floor tiles and wall tiles, waterproofing works, pergola and false ceiling, plumbing and drainage installations works, electrical works, rain water pipes, aluminium doors and windows, burglar proofing, timber openings, interior plants and site works and other miscellaneous works described in the bid documents.

3.External services installation works comprising rainwater installation works such as catch pits, gully traps, soak aways, waste water installation works such as manholes, channel manholes, septic tank, absorption pit, water supply works, electrical main supply and electric manholes. Works shall include reinstatement of damaged underground pipes and cables and other services that may be met with.

4. Provision of all piping including water supply, water tank, waste, floor traps, connection to   covered drain, soakaways, etc. as per Mechanical Engineer.

5.Hoarding shall be provided to secure contractor’s workspace and the site. Hoarding shall be to the satisfaction of the Project Architect and Project Structural Engineer.

6.Site works such as disabled parking, visitors parking, interlocking block, grass planting, CEB cubicle, pump room, garbage bins, boundary wall, green pavers, flower boxes,concrete platform for water tank, covered drains and landscaping and plants.

7.Works include reinstatement of damaged structures and finishes incidental to

construction works.

8.Other works as more fully described in the drawings, specifications and other

parts of the Bid document.

Participation is limited to citizens of Mauritius or entities incorporated in Mauritius. Joint Ventures should be among entities incorporated in Mauritius

  - Clarification if any may be requested from the public body.

  - Bidders are advised to carefully read the complete Bidding document, including the Particular Conditions of Contract in Section IV, before preparing their bids. The standard forms in this document may be retyped for completion but the Bidder is responsible for their accurate reproduction.

### 2.	Validity of Bids

The bid validity period shall be ninety (90) days from the date of bid submission deadline (bid preparation and submission) or up to 17 October 2020 whichever is later.

### 3.	Works Completion Period

The Intended Completion period is Two Hundred and Forty (240) days from start date of works.

### 4.        Site Visit

Bidders or their designated representatives are invited to attend a pre-bid meeting on [not applicable]. The purpose of the pre-bid meeting will be to clarify issues and to answer questions on any matter that may be raised at that stage.

### 5.	Sealing and Marking of Bids

Bids should be seal in a single envelop, clearly marked with the Procurement Reference Number, addressed to The SILWF with the bidders name at the back of the envelope.

6.	Submission of Bids

Bids should be deposited in the Bid Box located at The SILWF, 15-21 Edith Cavell Street, Port-Louis, not later than Monday 18 July 2022 at 10.00hrs.

Bids by post or hand delivery should reach above mentioned address by the same date and time at latest. Late bids will be rejected. Bids received by email will not be considered.

### 7.	Bid Opening

Bids will be opened by The SILWF at the Committee Room of The SILWF, 15-21 Edith Cavell Street, Port-Louis, on Monday 18 July 2022 at 10.10hrs. Bidders or their representatives may attend the bid opening if they choose to do so.

8.	Evaluation of Bids

The Public Body shall have the right to request for clarification during evaluation. Offers that are substantially responsive shall be compared on the basis of evaluated cost to determine the lowest evaluated bid.

### 9.	Eligibility Criteria

To be eligible to participate in this bidding exercise, Bidder should:

- have the legal capacity to enter into a contract to execute the works;

- be duly registered with the CIDB under the grade that would allow him to perform the value of works for which he is submitting his bid. (Note 1)

- not be insolvent, in receivership, bankrupt, subject to legal proceedings for any of    these circumstances or in the process of being wound up;

- not have had your business activities suspended;

- not be under a declaration of ineligibility by the Government of Mauritius in accordance with applicable laws at the date of the deadline for bid submission or appearing on the ineligibility lists of African Development Bank, Asian Development Bank, European Bank for Reconstruction and Development, Inter-American Development Bank Group and World Bank Group;

- not have a conflict of interest in relation to this procurement requirement; and

- have a Business Registration Card.

- Note 1 Sub-contractors undertaking works are also subject to registration with CIDB as     applicable to Contractors.

### 10.	Qualification and Experience Criteria

Bidders should have the following minimum qualifications and experience:

(a)	valid registration certificate with the CIDB under the grade that will enable the contractor to perform the works quoted for, under the following class(es): Building Construction Works .

(b)	experience in two works of a similar nature over the last 5 years, each of value not less than Twenty-Four Million (24.0 M) Rupees;

(c)	Contract Manager having as minimum qualification: A diploma in construction related field and 5 years  experience in the construction sector; or any equivalent qualifications acceptable to the Public body.

(d) 	minimum amount of liquid assets and/or credit facilities net of other contractual commitments of the Bidder of  Five Million (5.0 M) Rupees.

### 11.		Contents of bid

The Bid shall comprise the following:

(a)	All forms as provided on this bidding document and attachments required

(b)	Copies of report on the financial standing of the Bidder for the last three years, such as certified copies of Financial Statements or Audited Accounts as filed at the Registrar of Companies before the deadline set for submission of bids

(c)		Copy of Valid Registration certificate with the CIDB, as applicable

(d)		Copy of signed C.V of Contract Manager;

(e)	Copy of documentary evidence of liquid assets and/or credit facilities (Note 1);

(f)		Any other documents deemed necessary as per the requirements of this bidding document

Note 1

Bidders to demonstrate access to, or availability of, financial resources such as liquid assets, lines of credit, and other financial means, other than any contractual advance payments to meet the overall cash flow requirements for the contract and its current commitments. Documentary evidence may comprise but not limited to Bank certificate, Certificate from Auditors, Certificate from a Professional Accountant registered with MIPA, Certificate from Insurance companies.

12.   Joint Venture

Bids submitted by a joint venture of two or more firms as partners shall comply with the following requirements:

i. the Bid shall include all the information required as per the Qualification Information form for each joint venture partner;

ii. the Bid shall be signed so as to be legally binding on all partners;

iii. the Bid shall include a copy of the agreement entered into by the joint venture partners defining the division of assignments to each partner and establishing that all partners shall be jointly and severally liable for the execution of the Contract in 	accordance with the Contract terms; alternatively, a Letter of Intent to execute a 	joint venture agreement in the event of a successful bid shall be signed by all partners and submitted with the bid, together with a copy of the proposed agreement;

iv. one of the partners shall be nominated as being in charge, authorized to incur liabilities, and receive instructions for and on behalf of any and all partners of the joint venture; and

v. the execution of the entire Contract, including payment, shall be done 	exclusively with the partner in charge.

### 13.	Prices and Currency of Payment

Bidders should quote for the whole works. Prices for the execution of works shall be quoted and fixed in Mauritian Rupees. Items for which no rate or price is entered by Bidders, shall not be paid for by the Public Body when executed and shall be deemed covered by the other rates and prices in the Bills of Quantities.

Bids shall cover all costs of labour, materials, equipment, overheads, profits and all associated costs for performing the works, and shall include all duties. The whole cost of performing the works shall be included in the items stated, and the cost of any incidental works shall be deemed to be included in the prices quoted.  Bidders are required to submit their bid prices exclusive of VAT.

### 14.	Bid Securing Declaration

Bidders are required to subscribe to a Bid Securing Declaration in the Bid Submission Form.

### 15.	Margin of Preference

Margin of Preference shall not apply.

### 16. 	Award of Contract

The Bidder having submitted the lowest evaluated responsive bid and qualified to perform the works shall be selected for award of contract. Award of contract shall be by issue of a Letter of Acceptance in accordance with terms and conditions contained in Section IV: General Conditions of Contract and Particular Conditions of Contract.

### 17.	Performance Security and signing of contract

Within twenty-eight (28) days of the receipt of the Letter of Acceptance from the Employer, the successful Bidder shall furnish a Performance Security, in the amount equal to 10% of the Bid price (exclusive of VAT), in accordance with the conditions of contract, using for that purpose the Performance Security Form included in Section V Contract Forms.

The contract agreement shall be signed within 28 days after the successful bidder receives the letter of acceptance unless the parties agree otherwise.

Failure of the successful Bidder to submit the above-mentioned Performance Security or sign the contract within the required time may constitute sufficient grounds for the annulment of the award.

### 18.	Notification of Award and Debriefing

Prior to the expiration of the period of bid validity, the Employer shall, for contract amount above Rs 15 million, notify the selected bidder of the proposed award and accordingly notify unsuccessful bidders. Subject to Challenge and Appeal, the Employer shall notify the selected Bidder, in writing, by a Letter of Acceptance for award of contract. Until a formal contract is prepared and executed, the notification of award shall constitute a binding Contract.

The Public Body shall after award of contract, exceeding Rs 1 million and up to Rs 15 million, promptly inform all unsuccessful bidders in writing of the name and address of the successful bidder and the contract amount.

Furthermore, the Public Body shall attend to all requests for debriefing for contract exceeding Rs 1 million, made in writing within 30 days the unsuccessful bidders are informed of the award.

### 19. 	Advance Payment

The Public Body shall provide an Advance Payment on the Contract Price as stipulated in 	the General Conditions of Contract. The Advance Payment shall be guaranteed by an Advance Payment Security as per the format contained in Section V.

The Advance Payment shall be limited to 10% percent of the Contract Price, less any provisional and contingencies sums.

### 20.	Integrity Clause

The Public Body commits itself to take all measures necessary to prevent corruption and ensures that none of its staff, personally or through his/her close relatives or through a third party, will in connection with the bid for, or the execution of a contract, demand, take a promise for or accept, for him/herself or third person, any material or immaterial benefit which he/she is not legally entitled to.

### 21. 	Rights of Public Body

The Sugar Industry Labour Welfare Fund reserves the right:

(a)	to split the contract as per the lowest evaluated cost per lot; and

(b) 	to accept or reject any bid or to cancel the bidding process and reject all bids at any time prior to contract award without incurring any liability to the Public body.

### 22. 	Challenge and Appeal

Unsatisfied bidders shall follow procedures prescribed in Regulations 48, 49 and 50 of the Public Procurement Regulations 2008 to challenge procurement proceedings and award of procurement contracts or to file application for review at the Independent Review Panel.

    - The address, Tel. & Fax No... & Email address to file Challenges in respect of this procurement is:

The General Manager

Sugar Industry Labour Welfare Fund

15-21, Edith Cavell Street,

Port-Louis

Tel: 2122056

Fax:2089817

Email: silwf@intnet.mu

    - The address to file Application for Review is:

The Chairperson

Independent Review Panel,

5th Floor,

Belmont House

Intendence Street

Port Louis

| Tel : +230 2602228 Emal : irp@govmu.org |  |
| --- | --- |

Section II: Bidding Forms

SECTION II

Note: Bidders are required to fill all the forms in this section and submit as part of their bid. Non-submission of any form may lead to rejection of the bid

Bid Submission Form

Date: _______________

Bid’s Reference No.: _______________

Procurement Reference No:……………………

To:

We, the undersigned, declare that:

- We have examined and have no reservations to the Bidding Documents, including Addenda issued;

- We offer to execute in conformity with the Bidding Documents the following Works: ____________________________________________________________;

- The total price of our Bid excluding VAT is: _____________________(MUR):

- Our bid shall be valid for a period of ________ [Public body to insert validity period as specified in ITB 2] days from the date fixed for the bid submission deadline in accordance with the Bidding Documents or up to ………………., whichever is later,  and it shall remain binding upon us and may be accepted at any time before the expiration of that period;

- We hereby confirm that we have read and understood the content of the Bid Securing Declaration attached hereto and subscribe fully to the terms and conditions contained therein, if required. We understand that non-compliance to the conditions mentioned may lead to disqualification.

- If our bid is accepted, we commit to obtain a Performance Security in accordance with the Bidding Document;

- We, including any subcontractors or suppliers for any part of the contract, do not have any conflict of interest in accordance with ITB 8;

- We are not participating, as a Bidder in more than one bid in this bidding process;

- Our firm, its affiliates or subsidiaries, including any Subcontractors or Suppliers for any part of the contract, has not been declared ineligible under the laws of Mauritius;

- We have taken steps to ensure that no person acting for us or on our behalf will engage in any type of fraud and corruption as per the principles described hereunder, during the bidding process and contract execution:

- We shall not, directly or through any other person or firm, offer, promise or give to any of the Public Body’s employees involved in the bidding process or the execution of the contract or to any third person any material or immaterial benefit which he/she is not legally entitled to, in order to obtain in exchange any advantage of any kind whatsoever during the tender process or during the execution of the contract.

- We shall not enter with other Bidders into any undisclosed agreement or understanding, whether formal or informal. This applies in particular to prices, specifications, certifications, subsidiary contracts, submission or non-submission of bids or any other actions to restrict competitiveness or to introduce cartelisation in the bidding process.

- We shall not use falsified documents, erroneous data or deliberately not disclose requested facts to obtain a benefit in a procurement proceeding.

We understand that transgression of the above is a serious offence and appropriate actions will be taken against such bidders.

- We understand that this bid, together with your written acceptance, shall constitute a binding contract between us, until a formal contract is prepared and executed;

- We understand that you are not bound to accept the lowest evaluated bid or any other bid that you may receive; and

- If awarded the contract, the person named below shall act as Contractor’s Representative:

| Name: |  |
| --- | --- |
| In the capacity of: |  |
| Signed: |  |
| Duly authorized to sign the Bid for and on behalf of: |  |
| Date: |  |
| Seal of Company |  |

Appendix to Bid Submission Form

Bid Securing Declaration

By subscribing to the undertaking in the Bid Submission Form:

I/We accept that I/we may be disqualified from bidding for any contract with any Public Body for the period of time that may be determined by the Procurement Policy Office under section 35 of the Public Procurement Act, if I am/we are in breach of any obligation under the Bid conditions, because I/we:

- have modified or withdrawn my/our bid after the deadline for submission of  bids during  the period of bid validity specified by the Bidder in the Bid Submission Form; or

- have refused to accept a correction of an error appearing on the face of the bid; or

- having been notified of the acceptance of our bid during the period of bid validity, (i) have failed or refused to execute the Contract, if required, or (ii) have failed or refused to furnish the Performance Security, in accordance with the Instructions to Quote.

I/We understand this Bid Securing Declaration shall cease to be valid (a) in case I/we am/are  the successful bidder, upon our receipt of copies of the contract signed by you and the Performance Security issued to you by me/us ; or (b) if I am/we are not the successful Bidder, upon the earlier of (i) the receipt of your notification of the name of the successful Bidder; or (ii) thirty days after the expiration of the validity of my/our bid.

In case of a Joint Venture, all the partners of the Joint Venture shall be jointly and severally liable.

Qualification Information

| 1. Individual Bidders or Individual Members of Joint Ventures | 1.1 Constitution or legal status of Bidder: [attach copy] Place of registration: [insert] Principal place of business: [insert] |
| --- | --- |

1.2	Bidder shall provide (2) two works of a nature and amount similar to the Works performed as Contractor over the last 5 years.

| Project/Contract name and country | Name of client and contact person | Type of work performed and year of completion | Value of contract (national currency ) |
| --- | --- | --- | --- |
| (a) (b) |  |  |  |

|  | 1.3 Proposed subcontracts and firms involved. Refer to General Conditions of Contract Clause 7. |
| --- | --- |

| Sections of the Works | Value of subcontract | Subcontractor (name and address) | Experience in similar work |
| --- | --- | --- | --- |
| (a) (b) |  |  |  |

[Bidders have to ascertain that sub-contractors executing works are duly registered with the CIDB in accordance with CIDB Act 2008.

1.4	Name, address, and telephone, telex, and facsimile numbers of banks that may provide references if contacted by the Public Body. (Bidders to provide/upload)

2. Additional 	2.1 Bidders should provide any additional information Requirements                     requested in the Bidding Document.

Bills of Quantities for Bidders to Fill

| NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Item Number | Description | Unit of Measure | Qty | Rate | Amount |  |
|  |  |  |  |  | Rs | Cs |
| 1.0 | BILL NO.1 - PRELIMINARIES & GENERAL COSTS | - | 0 |  |  |  |
| 1.1 | NOTES | - | 0 |  |  |  |
| 1.2 | (i) The conditions of contract shall be the General Conditions of Contract (Works) as issued by the Procurement Policy Office and as amended in section Particular Conditions to the Contract (PCC). (ii) Bidders are referred to the abovementioned documents for the full intent and meaning of each clause thereof (hereinafter referred to the heading and clause number only) for which such allowance must be made as may be considered necessary. (iii) Bidders are strongly advised to price each item in the Preliminaries section of the Bills. Any item not priced shall not be paid by the Public Body and its cost shall be deemed covered by other rates and prices in the bidding documents. However, the contractor shall be responsible for ensuring all costs are included in conformity with the conditions of contract whether or not an item is listed. (iv) Where any item is not relevant to this specific contract, such item is marked N/A (signifying "not applicable"). | - | 0 |  |  |  |
| 1.3 | GENERAL CONDITIONS OF CONTRACT | - | 0 |  |  |  |
| 1.4 | The contractor shall refer to the conditions and particular conditions herein before mentioned for the intent and meaning of the clauses and allow whatever costs he may consider necessary against each clause together with sub-clauses in amplification of name. | - | 0 |  |  |  |
| 1.5 | General Conditons of Contract | - | 0 |  |  |  |
| 1.6 | A. General | - | 0 |  |  |  |
| 1.7 | Definitions | sum | 1 |  |  |  |
| 1.8 | Interpretation | sum | 1 |  |  |  |
| 1.9 | Language and Law | sum | 1 |  |  |  |
| 1.10 | Project Manager’s Decisions | sum | 1 |  |  |  |
| 1.11 | Delegation | sum | 1 |  |  |  |
| 1.12 | Communications | sum | 1 |  |  |  |
| 1.13 | Subcontracting | sum | 1 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 1.14 | Other Contractors | sum | 1 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1.15 | Personnel and Equipment | sum | 1 |  |  |  |
| 1.16 | Employer’s and Contractor’s Risks | sum | 1 |  |  |  |
| 1.17 | Employer’s Risks | sum | 1 |  |  |  |
| 1.18 | Contractor’s Risks | sum | 1 |  |  |  |
| 1.19 | Insurance | sum | 1 |  |  |  |
| 1.20 | Site Data | sum | 1 |  |  |  |
| 1.21 | Contractor to Construct the Works | sum | 1 |  |  |  |
| 1.22 | The Works to Be Completed by the Intended Completion Date | sum | 1 |  |  |  |
| 1.23 | Approval by the Project Manager | sum | 1 |  |  |  |
| 1.24 | Safety | sum | 1 |  |  |  |
| 1.25 | Discoveries | sum | 1 |  |  |  |
| 1.26 | Possession of the Site | sum | 1 |  |  |  |
| 1.27 | Access to the Site | sum | 1 |  |  |  |
| 1.28 | Instructions | sum | 1 |  |  |  |
| 1.29 | Appointment of the Adjudicator | sum | 1 |  |  |  |
| 1.30 | Procedure for Disputes | sum | 1 |  |  |  |
| 1.31 | B. Time Control | - | 0 |  |  |  |
| 1.32 | Program | sum | 1 |  |  |  |
| 1.33 | Extension of the Intended Completion Date | sum | 1 |  |  |  |
| 1.34 | Acceleration | sum | 1 |  |  |  |
| 1.35 | Delays ordered by the Project Manager | sum | 1 |  |  |  |
| 1.36 | Management Meetings | sum | 1 |  |  |  |
| 1.37 | Early warning | sum | 1 |  |  |  |
| 1.38 | C. Quality Control | - | 0 |  |  |  |
| 1.39 | Identifying defects | sum | 1 |  |  |  |
| 1.40 | Tests | sum | 1 |  |  |  |
| 1.41 | Correction of defects | sum | 1 |  |  |  |
| 1.42 | Uncorrected defects | sum | 1 |  |  |  |
| 1.43 | D. Cost Control | - | 0 |  |  |  |
| 1.44 | Contract Price | sum | 1 |  |  |  |
| 1.45 | Changes in contract price | sum | 1 |  |  |  |
| 1.46 | Variations | sum | 1 |  |  |  |
| 1.47 | Cash Flow Forecasts | sum | 1 |  |  |  |
| 1.48 | Payment Certificates | sum | 1 |  |  |  |
| 1.49 | Payments | sum | 1 |  |  |  |
| 1.50 | Compensation events | sum | 1 |  |  |  |
| 1.51 | Tax | sum | 1 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 1.52 | Currencies | sum | 1 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1.53 | Price Adjustment | sum | 1 |  |  |  |
| 1.54 | Retention | sum | 1 |  |  |  |
| 1.55 | Liquidated damages | sum | 1 |  |  |  |
| 1.56 | Bonus | sum | 1 |  |  |  |
| 1.57 | Advance Payment | sum | 1 |  |  |  |
| 1.58 | Securities | sum | 1 |  |  |  |
| 1.59 | Dayworks | sum | 1 |  |  |  |
| 1.60 | Cost of repairs | sum | 1 |  |  |  |
| 1.61 | Labour clause | sum | 1 |  |  |  |
| 1.62 | E. Finishing the Contract | - | 0 |  |  |  |
| 1.63 | Completion | sum | 1 |  |  |  |
| 1.64 | Taking over | sum | 1 |  |  |  |
| 1.65 | Final Account | sum | 1 |  |  |  |
| 1.66 | Operating and Maintenance Manuals | sum | 1 |  |  |  |
| 1.67 | Termination | sum | 1 |  |  |  |
| 1.68 | Fraud/ Corruption and Integrity Clause | sum | 1 |  |  |  |
| 1.69 | Payment upon Termination | sum | 1 |  |  |  |
| 1.70 | Property | sum | 1 |  |  |  |
| 1.71 | Release from Performance | sum | 1 |  |  |  |
| 1.72 | Particular Conditions of Contract | - | 0 |  |  |  |
| 1.73 | GCC 1.1 (r) | sum | 1 |  |  |  |
| 1.74 | GCC 1.1 (v) | sum | 1 |  |  |  |
| 1.75 | GCC 1.1 (y) | sum | 1 |  |  |  |
| 1.76 | GCC 1.1 (aa) | sum | 1 |  |  |  |
| 1.77 | GCC 1.1 (dd) | sum | 1 |  |  |  |
| 1.78 | GCC 1.1 (hh) | sum | 1 |  |  |  |
| 1.79 | GCC 2.2 | sum | 1 |  |  |  |
| 1.80 | GCC 2.3(i) | sum | 1 |  |  |  |
| 1.81 | GCC 3.1 | sum | 1 |  |  |  |
| 1.82 | GCC 5.1 | sum | 1 |  |  |  |
| 1.83 | GCC 8.1 | sum | 1 |  |  |  |
| 1.84 | GCC 13.1 | sum | 1 |  |  |  |
| 1.85 | GCC 13.3 | sum | 1 |  |  |  |
| 1.86 | GCC 13.7 | sum | 1 |  |  |  |
| 1.87 | GCC 14.1 | sum | 1 |  |  |  |
| 1.88 | GCC 20.1 | sum | 1 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 1.89 | GCC 23.1 | sum | 1 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1.90 | GCC 23.2 | sum | 1 |  |  |  |
| 1.91 | GCC 24. | sum | 1 |  |  |  |
| 1.92 | GCC 24.3 | sum | 1 |  |  |  |
| 1.93 | GCC 24.4 | sum | 1 |  |  |  |
| 1.94 | GCC 25.1 | sum | 1 |  |  |  |
| 1.95 | GCC 25.3 | sum | 1 |  |  |  |
| 1.96 | GCC 33.1 | sum | 1 |  |  |  |
| 1.97 | GCC 34.1 | sum | 1 |  |  |  |
| 1.98 | GCC 36.2 | sum | 1 |  |  |  |
| 1.99 | GCC 39.7 | sum | 1 |  |  |  |
| 1.100 | GCC 40.1 | sum | 1 |  |  |  |
| 1.101 | GCC 41.1 (l) | sum | 1 |  |  |  |
| 1.102 | PRELIMINARY PARTICULARS | - | 0 |  |  |  |
| 1.103 | Abbreviations | - | 0 |  |  |  |
| 1.104 | In these documents the following abbreviations shall have the meanings assigned to them respectively below: | - |  |  |  |  |
| 1.105 | BS: British Standards | - | 0 |  |  |  |
| 1.106 | MS: Mauritius Standards | - | 0 |  |  |  |
| 1.107 | CP: British Standard Code of Practice | - | 0 |  |  |  |
| 1.108 | Cu m or m3: Cubic metre | - | 0 |  |  |  |
| 1.109 | Sq m or m2: Square metre | - | 0 |  |  |  |
| 1.110 | LM or m: Linear metre | - | 0 |  |  |  |
| 1.111 | mm: Milimetre | - | 0 |  |  |  |
| 1.112 | Nr: Number | - | 0 |  |  |  |
| 1.113 | N: Newton | - | 0 |  |  |  |
| 1.114 | KN: Kilonewton | - | 0 |  |  |  |
| 1.115 | KG: Kilogram | - | 0 |  |  |  |
| 1.116 | (m/s): Measured separately elsewhere in these Bills of Quantities | - | 0 |  |  |  |
| 1.117 | n.e: Not Exceeding | - | 0 |  |  |  |
| 1.118 | dia.: Diameter | - | 0 |  |  |  |
| 1.119 | 150-300 mm (or similar expression) | - | 0 |  |  |  |
| 1.120 | As described | - | 0 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 1.121 | Approved , Directed or selected | - | 0 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1.122 | Units | - | 0 |  |  |  |
| 1.123 | All quantities and dimensions in the Bills of Quantities, Specifications and the Drawings are given in the "System International D'unites"(S.I Units) | - | 0 |  |  |  |
| 1.124 | Contracting and other Parties | - | 0 |  |  |  |
| 1.125 | Employer | - | 0 |  |  |  |
| 1.126 | The term "Employer" shall mean the Sugar Industry Labour Welfare Fund | - | 0 |  |  |  |
| 1.127 | Project Manager | - | 0 |  |  |  |
| 1.128 | The term "Project Manager" shall mean the Sugar Industry Labour Welfare Fund | - | 0 |  |  |  |
| 1.129 | Architect | - | 0 |  |  |  |
| 1.130 | The term "The Architect" shall mean Ministry of National Infrastructure and Community Development, Technical Division, Phoenix | - | 0 |  |  |  |
| 1.131 | Civil/Structural Egineer | - | 0 |  |  |  |
| 1.132 | The term "The Civil and Structural Engineer" shall mean Ministry of National Infrastructure and Community Development, Technical Division, Phoenix | - | 0 |  |  |  |
| 1.133 | Quantity Surveyor | - | 0 |  |  |  |
| 1.134 | The term "The Quantity Surveyor" shall mean Ministry of National Infrastructure and Community Development, Technical Division, Phoenix | - | 0 |  |  |  |
| 1.135 | Mechanical Engineer | - | 0 |  |  |  |
| 1.136 | The term "The Mechanical Engineer" shall mean Ministry of National Infrastructure and Community Development, Technical Division, Phoenix | - | 0 |  |  |  |
| 1.137 | Electrical Engineer | - | 0 |  |  |  |
| 1.138 | The term "The Electrical Engineer" shall mean Ministry of National Infrastructure and Community Development, Technical Division, Phoenix | - | 0 |  |  |  |
| 1.139 | PROJECT PARTICULARS | - | 0 |  |  |  |
| 1.140 | Location of the Works | - | 0 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 1.141 | The site Works is located at Gokhoola as shown on the location plan Drawing No G859/SW/03 | - | 0 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1.142 | General description of the works | 0 | 0 |  |  |  |
| 1.143 | The Project shall consist of the construction of a new single storey building in reinforced concrete frame and blockwork and R.C roof slab covered with waterproofing as per drawings and specifications and complete with all services and site works and other miscellaneous works as described in the bid documents. | - | 0 |  |  |  |
| 1.144 | Preliminary Investigation | - | 0 |  |  |  |
| 1.145 | The contractor is advised to visit the site before submitting his tender and ascertain the nature of the ground and subsoil to be excavated, the contours thereof and acquaint himself with local conditions, site conditions, site restrictions, working space available, means of access, limitations and restrictions to access, risk of damage to adjacent properties, roads, etc., the full extent and and character of the operations, the facilities for obtaining the articles or materials for the works, the supply of labour and other matters affecting the execution of the Contract generally, as no claim whatsoever on the grounds of want of knowledge in such respect will be allowed. The Contractor shall carry out any other survey that in his opinion is necessary for him to submit a proper bid. This survey shall also include the services underground or above that may run on site and he shall allow in his offer for their deviations if required. | Sum | 1 |  |  |  |
| 1.146 | The contractor shall be deemed to have examined any site data made available and suplemented by any information. The Contractor shall, however, be responsible for interpreting all such data. | Sum | 1 |  |  |  |
| 1.147 | GENERAL SPECIFICATION AND OTHER DOCUMENTS | - | 0 |  |  |  |
| 1.148 | Generally | - | 0 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 1.149 | The General Specifications are included in Appendix 1 of the Bidding documents. Where the General Specifications contain clauses related to any of the following General Requirements, these Bills of Quantities refer to those clauses in the General Specifications. | - | 0 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1.150 | The Contract Bills have been prepared in accordance with the Principles of Measurement International (POMI) for Works of Construction June 1979 Edition, issued by the Royal Institution of Chartered Surveyors, as may be amended by the special requirements of these Bills of Quantities. | - | 0 |  |  |  |
| 1.151 | These principles of measurement must be accepted and will be strictly adhered to for cinsistency in carrying out measurement of variation works and remeasurement as necessary. | - | 0 |  |  |  |
| 1.152 | All references to methods or principles or clarification of messurement in the "Specifications" shall be deemed to have been deleted. | - | 0 |  |  |  |
| 1.153 | The drawings which were used in the preparation of these Bills of Quantities are listed in the Drawing No G859/SW/03 &G859/SW/ST01 | - | 0 |  |  |  |
| 1.154 | The Contractor will be deemed to have examined these drawings and to have ascertained their details and the nature of the works and no claim for want of knowledge will be entertained. | Sum | 1 |  |  |  |
| 1.155 | Specific Nature of Project | - | 0 |  |  |  |
| 1.156 | Bills of Quantities | - | 0 |  |  |  |
| 1.157 | No unauthorised alteration in any of these Bills of Quantities is to be made by the Bidders. Should any alteration, amendment, note or addition be made, it will not be recognised but the reading as printed will be adhered to. | - | 0 |  |  |  |
| 1.158 | Bidders should quote for the whole works. Prices for the execution of works shall be quoted and fixed in Mauritian Rupees. Items for which no rate or price is entered by the Contractor, shall not be paid for by the Public Body when executed and shall be deemed covered by the other rates and prices in the Bills of Quantities. | - | 0 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 1.159 | The Contractor is advised that the quantities, sizes, etc., contained in these Bills of Quantities should not be used for the purpose of ordering materials without checking from the working drawings or from site, as no claim will be entertained for costs incurred in over-or-under-ordering of materials. | - | 0 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1.160 | All prices or rates inserted in these Bills of Quantities are to be fully inclusive prices or rates for the finished work described under the respective items and/or drawings, unless otherwise stated or unless there is a separate item for extra labour, cutting or waste and are to include for all materials, making, conveying, cartage, carriage and delivery, unloading, storing, unpacking, hoisting or conveying, setting, fixing and building into position and labour of every description, cutting and waste, templates, patterns and models, plant, temporary works, return of packings, taxes, levies, custom duties, surchages, establishment charges, overheads, costs of all nature, and all obligations arising out of the Conditions of Contract, the provisions of Material and Workmanship bills, the provisions of the Preliminaries bills and the execution of the relevant work. Price for plant, temporary works, services and other items provided shall include for the supply, maintenance, fuel, operating costs and subsequent removal and making good as necessary. | Sum | 1 |  |  |  |
| 1.161 | The prices for all items shall where applicable include for all small quantities, short lengths and narrow widths. | - | 0 |  |  |  |
| 1.162 | Where items are described as "Fix only" this shall be deemed to mean unloading on site, storing, unpacking, distributing to the required position on site, assembling and fixing, and returning packing cases to consignor if required. | - | 0 |  |  |  |
| 1.163 | The Contractor shall be held solely responsible for and shall, at his own expense, rectify any errors arising out of incorrect interpretation of the Drawings, Specifications, Bill of Quantities or instructions. | - | 0 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 1.164 | The Contractor shall note that no claims whatsoever will be allowed in respect of errors or omissions in pricing due to brevity of descriptions of items in the Bills of Quantities which are fully described when read in conjunction with the relevant requirements of this Bill and Specifications and/or the Conditions of Contract and/or drawings and any other conditions of the bidding documents. | - | 0 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1.165 | Shop Drawings | - | 0 |  |  |  |
| 1.166 | The term "shop drawings" shall mean drawings, diagrams, schedules, performance charts, brochures, operating manuals and other data which are prepared by the Contractor or any subcontractor, manufacturer or supplier and which illustrate some portion of the Works and help identify how they will fit into the structure. The Contractor shall prepare, at his own expense, and shall submit two copies of shop drawings of all fabricated work, working or setting out drawings, shop details and schedules to the Project Manager for approval by the Project Manager and such work shall not be executed by the Contractor until approved. The Contractor shall present a complete schedule showing submission dates, for all trades and the scheduled dates, for approval of all drawings. The Contractor shall note that the Project Manager requires two weeks for checking from the date of the receipt of all shop drawings. | - | 0 |  |  |  |
| 1.167 | All submissions shall be on dates as indicated in the above schedule and sufficiently in advance as no claim for Extension of the Time for Completion will be granted to the Contractor by reason of his failure in this respect. | Sum | 1 |  |  |  |
| 1.168 | The contractor shall submit to the Project Manager two copies of catalogues and data for approval. The Contractor shall check all submissions for conformity with the contract drawings and specifications and correct any errors, omissions or deviations before forwarding to the Project Manager. | Sum | 1 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 1.169 | The Project Manager's approval of any document or drawing does not in any way vary his contractual obligations and liabilities to the owner or any other party, nor does it vary the contractual obligations and liabilities of the party submitting such document or drawing for approval. | - | 0 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1.170 | Corrections of shop drawings by the Project Manager shall not change the scope of Works. Should any such correction constitute a change of scope of Works, the Contractor shall notify the Project Manager in writing within not more than seven (7) calender days of such change and shall not proceed with the fabrication until so authorised by the Project Manager. | - | 0 |  |  |  |
| 1.171 | As- Made Drawings |  |  |  |  |  |
| 1.172 | The Contractor shall submit upon completion of the works, as made drawings including manuals as more fully specified in the contract documents in hard and soft copies properly arranged and with correct labelling. | Sum | 1 |  |  |  |
| 1.173 | FINANCIAL ASPECTS |  |  |  |  |  |
| 1.174 | Dayworks |  |  |  |  |  |
| 1.175 | Variations including variations to Contractor's work will be valued on a daywork basis only if so authorised in writing by the Project Manager. The Contractor must present a full detailed account of labour and materials expended in the execution of day work variations which must be signed by the Project Manager before the end of the week following that in which the work was executed, failing which the claims will be disallowed. | Sum | 1 |  |  |  |
| 1.176 | Notwithstanding anything which is or may be stated to the contrary, the signature of the Project Manager or any other consultant shall only indicate that the work has been carried out but shall not indicate acceptance of quantum, value or method of valuation of work executed thereunder nor shall such signature indicate acceptance that such work constitutes a variation. The quantum of this work and the method of valuation of same will be decided by the Project Manager or the Quantity Surveyor. | - | 0 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 1.177 | Final Account | - | 0 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1.178 | The Contractor shall timeously supply the Project Manager with a detailed account for the purpose of enabling the Project Manager to compile the Final Account. If the account submitted by the Contractor is not correct and complete, the Contractor shall make all necessary corrections or additions as directed by the Project Manager. | Sum | 1 |  |  |  |
| 1.179 | OBLIGATIONS AND RESTRICTIONS IMPOSED BY THE EMPLOYER | - | 0 |  |  |  |
| 1.180 | Site Boundaries | - | 0 |  |  |  |
| 1.181 | The site shall be defined by the boundaries shown on the Architect's dawings. The Contractor shall submit for approval to the Project Manager prior to start of works a site organisation layout including the area of the site which may be occupied by the Contractor for his use as storage or for erection of site offices. | Sum | 1 |  |  |  |
| 1.182 | Access to Site and Temporary Roads | - | 0 |  |  |  |
| 1.183 | The access to the site shall be as shown on the Architect's drawings and/or as agreed with the Project Manager prior to commencement of the work. The Contractor must allow here for building and maintaining any temporary access roads, gantries for the transport and lifting of all materials, plants and workmen required for the complete execution of the works, working space, storage accomodation, the nature of the ground proximity of adjoining structures and roads local regulations requirements and any other limitations imposed by the site and its surroundings including the provision of temporary culverts, crossing bridges or other means of gaining access to the site, and obtaining any wayleaves required. Upon the completion of the works the Contractor shall leave such temporary access roads, culverts, fences etc undisturbed unless ordered otherwise by the Project Manager. No claims will be entertained for such temporary services left on site or for their removal and restoration on the site to the original condition. | Sum | 1 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 1.184 | Maintenance of Roads | - | 0 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1.185 | The Contractor shall allow for maintaining and keeping public and private roads free from mud debris, etc., arising from the works throughout the duration of the contract. | Sum | 1 |  |  |  |
| 1.186 | Site Conditions and Working space | - | 0 |  |  |  |
| 1.187 | The Contractor is advised that working space on site is restricted to the site boundaries of the works. He shall erect temporary hoarding at the site boundary and he shall not encroach beyond such defined boundaries or areas of operation. The Contractor shall take special care not to disturb or hinder the flow of all traffic in any way whatsoever and shall allow for the unimpeded flow and operation of traffic whether vehicular or pedestrian, failing which he may be liable for any costs or any loss or damages incurred as a result thereof. He shall allow here or in his rates for the costs of the necessary measures that such restriction may entail. | Sum | 1 |  |  |  |
| 1.188 | Site to be tidy |  |  |  |  |  |
| 1.189 | The site shall be maintained in a neat, tidy and healthy condition and the Contractor shall remove all surplus spoil, waste and unwanted materials, debris and other litter from the site from day to day or as directed by the Project Manager. | Sum | 1 |  |  |  |
| 1.190 | Program | - | 0 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 1.191 | The Contractor is to prepare and submit to the Project Manager within the time stated in the contact after the date of the Letter of Acceptence two copies of the Program showing the general methods, arrangements, order, and timing of all activities in the works. The submission of any drawings and samples for approval shall be in accordance with the Program allowing sufficient time for consideration, comment and modification before approval, so that manufacture and installation are not delayed. The Program shall include the planned monthly rates of progress between the programmed date for commencement and completion for all items of work for various stages of construction including dates by which major drawings requiring approval will be submitted. The Program shall be in the form of a time and progress chart or a critical path network and shall also show a weekly schedule of labour and plant resources to be employed for each item of work of the Program. | Sum | 1 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1.192 | The Contractor shall also submit to the Project Manager at regular intervals updated programs for approval. | Sum | 1 |  |  |  |
| 1.193 | The Program shall reflect the agreed completion date of the Works as set out in the Contract and shall indicate anticipated starting and completion dates for the various trades and the various sections of the Works. | Sum | 1 |  |  |  |
| 1.194 | The Project Manager's approval of the program shall not alter the contractor's obligations | - | 0 |  |  |  |
| 1.195 | The Contractor shall ensure that the work is carried out and controlled in such a way that the Contract is completed by the completion date. Failure by the Contractor to submit an updated program within the time specified in the Contract will result in the retention of the amount stated in the contract from the next payment certificate and same will continue until the next payment after the date on which the overdue program has been submitted. | Sum | 1 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 1.196 | Discrepancies | - | 0 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1.197 | Should the contractor at any time discover discrepancies between drawings, scope of works or any other documents or in dimensions, instructions, he shall immediately refer same to the Project Manager who shall decide the course to be followed. Failure on the part of the Contractor to comply with this clause may invalidate any subsequent claim made by him. | Sum | 1 |  |  |  |
| 1.198 | Setting Out | - | 0 |  |  |  |
| 1.199 | The Contractor shall set out the works in accordance with the dimensions and levels shown on the approved drawings and shall be responsible for the correctness of all dimensions and levels so set out by him. He will be required to rectify all errors arising from inaccurate setting out at his own cost and expense. In the event of errors or discrepancies in the dimensions or levels marked out on the drawings being discovered , such errors or discrepancies shall be reported by the Contractor to the Project Manager for his immediate consideration. | Sum | 1 |  |  |  |
| 1.200 | No work connected with such errors and/or discrepancies shall be continued by the Contractor until he has received written instructions from the Project Manager to adjust such errors and/or discrepancies. | - | 0 |  |  |  |
| 1.201 | Area of operations | - | 0 |  |  |  |
| 1.202 | Provide for taking reasonable precautions to prevent all workpeople, including those employed by other contractors from encroaching or trespassing upon any part of the site or premises which are not affected by the Works and from trespassing upon adjoining and existing owner's property except where permission be granted to facilitate the carrying out of the works. | Sum | 1 |  |  |  |
| 1.203 | The Contractor shall be required to limit the construction activity, temporary building, storage or equipment and materials, etc., within the boundaries of the area allocated to him. | Sum | 1 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 1.204 | Materials or object of value found on site | - | 0 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1.205 | Any materials or objects of historical value or other interest or of significant values such as buried relics and the like, including sand or gravel found on site when excavating are to remain the property of the Employer under this Contract and shall only be removed as the Project Manager shall direct and access shall be allowed only to any authorized person instructed to remove same. | Sum | 1 |  |  |  |
| 1.206 | Compliance with Statutory/Public Authorities | - | 0 |  |  |  |
| 1.207 | The Contractor shall comply with all terms and conditions imposed by the statutory Authorities and any other authorities for this project, and shall allow herein for all costs in compliance thereof. | Sum | 1 |  |  |  |
| 1.208 | The Contractor shall comply with the requirements and conditions defined in the Environment Impact Assessment Report as appropriate and shall allow for all costs in connection herewith. Particular attention is drawn to working hours and hoarding and protection requirements affecting neighbouring sites. | Sum | 1 |  |  |  |
| 1.209 | Hoardings | - | 0 |  |  |  |
| 1.210 | The Contractor shall provide for all necessary hoardings, guardrails, gates and the likes along the boundaries allocated to him in order to secure the site and protect the public and the occupants of the existing and adjoining properties. The Contractor shall comply with the requirements of any relevant authorities and to the full satisfaction of the Project Manager. The Contractor shall allow for the removal and making good any damage resulting therefrom on completion. | Sum | 1 |  |  |  |
| 1.211 | Protection of Existing Structures, Services and Features | - | 0 |  |  |  |
| 1.212 | The Contractor shall allow for taking all necessary precautions in order to protect efficiently all existing buildings, structures, services, features and the like against any pollution arising out of or by reasons of the execution of the works. | Sum | 1 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 1.213 | CONTRACTOR'S ADMINISTRATIVE ARRANGEMENTS | - | 0 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1.214 | Safety on Site | - | 0 |  |  |  |
| 1.215 | The Contractor shall take all necessary steps and shall be fully responsible and liable to ensure that the site activities are undertaken in an orderly manner and that all safety precautions are enforced at all times to avoid accidents to the personnel of the Contractor, other parties working on site, the employer's representatives and other authorised person and take all necessary measures for the safety of the public and property. The Contractor shall be responsible for the health and safety of all activities on site and shall comply with the relevant legislations regarding health and safety on site, including the Occupational Safety and Health (Safety of Scaffold) Regulations 2013. | Sum | 1 |  |  |  |
| 1.216 | Government Ordinance and Regulations | - | 0 |  |  |  |
| 1.217 | The Contractor shall make himself acquainted with current ordinance and regulations, statutes, Industrial Agreements applicable to the construction industry and all his obligations at law which may affect the organization of works, supply and control of labour, etc and allow accordingly in his Tender. No claim for want of knowledge in this connection will be entertained. | Sum | 1 |  |  |  |
| 1.218 | Discharge of Workmen | - | 0 |  |  |  |
| 1.219 | The Contractor shall only employ qualified, competent and experience site managers/supervisors/engineers/contract managers/foremen and so on and all necessary backup staff who are skilled, competent and experienced in their respective callings. If in the opinion of the Project Manager any person employed by the Contractor misconducts himself or is likely to cause or has caused strikes, quarrel or delays, or is incompetent, the Contractor when so directed by the Project Manager in writing shall, within the time specified in the contract, remove such person from the work site. The person shall have no further connection with the work in the contract. | Sum | 1 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 1.220 | Site Management Costs | - | 0 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1.221 | The Contractor shall provide for all on and off-site management costs. | Sum | 1 |  |  |  |
| 1.222 | The contractor shall provide at the start of the contract an organisation chart showing a complete and detailed list of his site supervisory personnel for the project for the approval of the Project Manager. The list shall include all relevant details of each member of the team including his qualification and experience, functions, position and duties. The provision of such chart and the Project Manager's approval thereof shall not limit the Contractor's responsibilities and obligations in respect of the adequacy of personnel on the site. In the event additional staff is considered necessary to supervise the execution of the works efficiently and effectively, the Contractor shall provide such additional staff at his own costs. | Sum | 1 |  |  |  |
| 1.223 | Site Meetings | - | 0 |  |  |  |
| 1.224 | The Project Manager may hold site meetings on a regular basis and the Contractor shall arrange to attend such meetings when required and shall allow here for all expenses in connection with his own attendance including for the provision of suitable accommodation. | Sum | 1 |  |  |  |
| 1.225 | The Contractor shall on a regular basis also hold meetings with his employees, sub-contractors and suppliers for the proper monitoring of their progress and the coordination of all aspects of the contract. | Sum | 1 |  |  |  |
| 1.226 | Watching and lighting | - | 0 |  |  |  |
| 1.227 | The Contractor, from the commencement of the contract, shall provide all watching, lighting and protection of the works, materials and plant and the protection of the public including the prevention of unauthorised access to adjoining and existing property from the site of works and the provision of facilities for any person employed by the Contractor to provide such security. | Sum | 1 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 1.228 | Protection and Delivery | - | 0 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1.229 | The Contractor shall allow for covering up and protection of work liable to damage in every respect including temporary roofs, gutters, drains, and so on. If necessary, case up, cover, or in other suitable way protect all finished work liable to damage to the satisfacton of the Project Manager until completion of the contract. The Contractor shall, at his own cost, make good to any damage caused by adverse weather or otherwise. On completion the whole of the works shall be delivered up clean, complete and perfect in every respect to the satisfaction of the Project Manager. | Sum | 1 |  |  |  |
| 1.230 | Transport for Workforce | - | 0 |  |  |  |
| 1.231 | Allow for all expenses including but not limited to travelling expenses and fares in connection with transport of workforce to and from and around the site. | Sum | 1 |  |  |  |
| 1.232 | Ordering of Items | - | 0 |  |  |  |
| 1.233 | The contractor shall place order at the very beginning of the contract for materials , fittings, items of equipment and so on required for this work. Non-availabaility of these items or in the quantity required will not be considered as an excuse for delay on the works. | Sum | 1 |  |  |  |
| 1.234 | Labour On-Costs | - | 0 |  |  |  |
| 1.235 | Allow for all disbursements arising from the employemnt of labour induding compliance with the provisions of the Employment Act and Regulations including but not limited to : | Sum | 1 |  |  |  |
| 1.236 | (i) National Pension Contribution, training levy, contribution to Employee's Welfare Fund, | Sum | 1 |  |  |  |
| 1.237 | (ii) sick leave | Sum | 1 |  |  |  |
| 1.238 | (iii) annual and public holidays, | Sum | 1 |  |  |  |
| 1.239 | (iv) travelling time, subsistence expences and fares and the likes, | Sum | 1 |  |  |  |
| 1.240 | (v) non-productive time and other expenses in connection with overtime, | Sum | 1 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 1.241 | (vi) shutdown on account of cyclonic and adverse weather conditions, | Sum | 1 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1.242 | (vii) End of year bonus, | Sum | 1 |  |  |  |
| 1.243 | (viii) incentive and bonus payments, | Sum | 1 |  |  |  |
| 1.244 | (ix) severance pay and obligations and workmen's compensation insurance, | Sum | 1 |  |  |  |
| 1.245 | (x) protective clothing and equipment, | Sum | 1 |  |  |  |
| 1.246 | (xi) Any other items not listed above but which are deemed to be included under this heading shall be allowed here. | Sum | 1 |  |  |  |
| 1.247 | Overtime | - | 0 |  |  |  |
| 1.248 | No claim will be entertained in connection with any overtime incurred by the Contractor in order to maintain progress and ensure completion of the works within the contract period. | Sum | 1 |  |  |  |
| 1.249 | Site Transport Services | - | 0 |  |  |  |
| 1.250 | Provide all vehicles necessary for the efficient and expedious execution of the works including but not limited to the following: | Sum | 1 |  |  |  |
| 1.251 | Transport of temporary accommodation to/from site | Sum | 1 |  |  |  |
| 1.252 | Transport of mechanical/construction plant to/from site | Sum | 1 |  |  |  |
| 1.253 | Transport of small plant to/from site | Sum | 1 |  |  |  |
| 1.254 | Transport of scaffolding to/from site | Sum | 1 |  |  |  |
| 1.255 | Site trucks | Sum | 1 |  |  |  |
| 1.256 | Tractors and trailers | Sum | 1 |  |  |  |
| 1.257 | Dumpers | Sum | 1 |  |  |  |
| 1.258 | Buses | Sum | 1 |  |  |  |
| 1.259 | Vans | Sum | 1 |  |  |  |
| 1.260 | Staff cars | Sum | 1 |  |  |  |
| 1.261 | At or before completion, the Contractor shall clear same from building and site and make all good. | Sum | 1 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 1.262 | MECHANICAL PLANT/CONSTRUCTION PLANT AND HOISTING | - | 0 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1.263 | The Contractor shall provide all necessary plant and equipment including mechanical plant and non-mechanical plant, small plant, tools, scaffolding and gantries, vehicles, batching plant, cranes, loading platforms, Hoists, lifts, pumps, electrical generators, air-compressors, and others and maintenance of same. | Sum | 1 |  |  |  |
| 1.264 | The Contractor shall, at or before completion, clear same including rubbish and unused materials from building and site and make all good. | Sum | 1 |  |  |  |
| 1.265 | The Contractor shall also allow for the removal of all rubbish and dirt from the site as it accumulates at the discretion of the Project Manager. | Sum | 1 |  |  |  |
| 1.266 | EMPLOYER'S FACILITIES | - | 0 |  |  |  |
| 1.267 | The Contractor is to allow for the costs of facilities on site but not limited to the following: | Sum | 1 |  |  |  |
| 1.268 | Sign Board | - | 0 |  |  |  |
| 1.269 | Provide site signboard for the display of the project title and the names and addresses of the Employer and his consultants and the Contractor's name all in accordance with the relevant Artchitect's drawing. The Contractor shall also allow here for obtaining all clearances from the relevant Authority and shall dismantle and remove same from site after completion of works including making all good. | Sum | 1 |  |  |  |
| 1.270 | Site Accommodation | - | 0 |  |  |  |
| 1.271 | The Contractor shall provide, effect and maintain where directed on the site an approved weather and sunproof temporary office for the sole use of the Employer's representatives. | Sum | 1 |  |  |  |
| 1.272 | The Contractor shall upon completion dismantle and clear away same and make all good. | Sum | 1 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 1.273 | The office shall be of good quality, well ventilated, suitable standard and size and shall be fitted with a table and chairs to accommodate 10-15 persons, one pin board 1mx1.5m, First Aid, toilets, one filing cabinet and complete with all other necessary services and facilities. | Sum | 1 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1.274 | Allow for cleaning of the office on a regular basis and as required. | Sum | 1 |  |  |  |
| 1.275 | Survey and Testing equipment | - | 0 |  |  |  |
| 1.276 | As may be necessary on site. | Sum | 1 |  |  |  |
| 1.277 | CONTRACTOR'S FACILITIES | - | 0 |  |  |  |
| 1.278 | Temporary Accomodation | - | 0 |  |  |  |
| 1.279 | The Contractor shall provide, effect and maintain good quality/suitable standard temporary accomodation including sanitary accomodation to the requirement of the Health and Safety Act and Labour Act, messroom and other facilities and services for all workers and staff working on the project including those engaged by the Employer where applicable of suitable size for the number of workers employed, all to the approval of the Project Manager. The Contractor shall allow for regular cleaning of the accommodation. | Sum | 1 |  |  |  |
| 1.280 | The Contractor shall upon completion of the works dismantle and clear away same and make all good. | Sum | 1 |  |  |  |
| 1.281 | Sheds for Storage of materials | - | 0 |  |  |  |
| 1.282 | The Contractor shall provide and maintain to the satisfaction of the Project Manager and clear away on completion of the works, water tight sheds for the storage and protection of all materials required for the proper execution of the works. | Sum | 1 |  |  |  |
| 1.283 | Use of the New Construction | - | 0 |  |  |  |
| 1.284 | The Contractor shall not be allowed to use any part of the new constuction for any purpose whatsoever. | Sum | 1 |  |  |  |
| 1.285 | Use of Existing Services | - | 0 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 1.286 | No connection to existing services such as existing electricity supply and water supply and other existing services shall be permitted. | Sum | 1 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1.287 | Water, lighting and Power, Telephone | - | 0 |  |  |  |
| 1.288 | The Contractor shall provide at his own risk and cost the water, light and power required for use in the work and make them free of charge to others authorised on site. The Contractor will be required to arrange with the relevant authority for the installation of a temporary connection to the main water supply and to provide himself with all necessary temporary water distribution piping and storage tanks, plumbing and so on as required and shall remove same and make good disturbed surfaces at completion of the works to the satisfaction of the Project Manager and pay all charges in connection therewith including for the meter hire and water consumed until completion of the works. | Sum | 1 |  |  |  |
| 1.289 | The Contractor shall arrange for the provision of all lighting and power with the relevant authority for use on the works and provide all necessary connecion including switchgear, distribution board, etc and alter or adapt or remove and make good on completion of the works and pay all charges for meter hire and consumption until completion of the works. | Sum | 1 |  |  |  |
| 1.290 | The Contractor shall provide and maintain a temporary telephone service on site for the full period of the contract at his own costs. | Sum | 1 |  |  |  |
| 1.292 | Site Diary and Site Records | - | 0 |  |  |  |
| 1.293 | The Contractor shall keep daily logs of his work progress including records of weather conditions and all site information such as the number of workers in various trades, plant and equipment details, materials delivered to the site, the quantity used and retained, complaints, accidents or incidents and others. The diary shall be in a format approved by the Project Manager and shall be available at all times for inspection. Copies of such records shall be submitted to the Project Manager at regular intervals agreed. | Sum | 1 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 1.294 | The Contractor shall also keep and provide records of site levels, surveys, test reports etc as directed. | Sum | 1 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1.295 | MISCELLANEOUS AND GENERAL ITEMS | - | 0 |  |  |  |
| 1.296 | Insurances | - | 0 |  |  |  |
| 1.297 | The Contractor shall effect, maintain and renew (where requried) all insurances and in respect to all specified perils as required under this contract and shall also provide for the submission of copies of all premium receipts to the Project Manager timely. | Sum | 1 |  |  |  |
| 1.298 | Notwithstanding anything to the contrary in the contract agreement, the Contractor shall indemnify and held harmless the Employer from any claims brought by or on hebalf of third parties against it, its préposés and/or agents for any loss or damage caused to third parties or on their behalf by the acts and omission of the Contractor or its employees, préposés and/or agents during the execution of the works pursuant to the contract agreement. | Sum | 1 |  |  |  |
| 1.299 | Notwithstanding anything to the contrary in the contract agreement, the Employer shall be entitled to claim from the Contractor such loss and damages caused to it by the acts or omissions of the Contractor, its employees, préposés and/or agents. | Sum | 1 |  |  |  |
| 1.300 | Performance Security | - | 0 |  |  |  |
| 1.301 | The Contractor shall provide a performance security in which every aspect of the Contractor's performance is guaranteed all as expressed in this contract. | Sum | 1 |  |  |  |
| 1.302 | Protection of Adjoining Properties | - | 0 |  |  |  |
| 1.303 | The Contractor shall provide for the protection of adjoining properties including walls, roofs, windows, footings, fences, landscape and other and shall ensure the security and protection of the public. The Conractor shall also take all precautions required to avoid interference and to prevent inconveniences, nuisances of any kind and injuries to the holders or occupiers of adjoining or surrounding properties. | Sum | 1 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 1.304 | The Contractor shall at all times from the start to completion of the works, keep all roads, paths and the likes affected by the works in a safe and clear state and shall use all proper precautions to ensure the safety of all users. | Sum | 1 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1.305 | The Contractor shall indemnify and held the Employer harmless against and from all damages, losses, and expenses (including legal fees and expenses) in connection therewith. | Sum | 1 |  |  |  |
| 1.306 | Occupational Health and Safety | - | 0 |  |  |  |
| 1.307 | The Contractor shall ensure that all necessary precautions are taken at all times, to secure the health, safety and welfare of all persons, whether in his employment or otherwise, upon the site and comply with all current regulations in force in the country. The Contractor shall provide for medical and attendants (if required ), first aid materials, safety equipment, special clothing, safety officer and so on. | Sum | 1 |  |  |  |
| 1.308 | Final Clearance and Hand Over | - | 0 |  |  |  |
| 1.309 | The Contractor shall provide for the costs of final cleaning and cleaning of building and surrounding areas prior to handing over to the full satisfaction of the Project Manager. | Sum | 1 |  |  |  |
| 1.310 | Maintenance of Public and Private Roads , Drains and Services | - | 0 |  |  |  |
| 1.311 | The Contractor shall allow for protecting, upholding and maintaining public and private roads including footpaths, kerbs, live drainage etc, water sewer pipes and other main ducts, power services, overhead cables, etc whether on or off the site during the execution of the works. The Contractor shall ascertain the position of all such structures and services and no claim for want of knowledge shall be entertained. The Contractor shall make good any damage caused at his own costs including paying any charges and other associated costs in connection therewith. | Sum | 1 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 1.312 | Traffic Regulations and requirements | - | 0 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1.313 | The Contractor shall allow for the compliance with all rules and regulations such as police regulations , or requirements concerning vehicular traffic control, pedestrian control, site access and egress, safety measures and any other matter affecting the works. | Sum | 1 |  |  |  |
| 1.314 | Testing | - | 0 |  |  |  |
| 1.315 | The Contractor shall allow for all costs associated with the provision of apparatus, documents , assistance, etc as are necessary to carry out all tests specified efficiently. In addition laboratory tests of basic materials such as aggregates, concrete crushing strength of blocks, etc shall be required. The tests themselves should be carried out by an approved laboratory and all charges shall be borne by the Contractor. The Contractor shall submit all test reports to the Project Manager. | Sum | 1 |  |  |  |
| 1.316 | Samples | - | 0 |  |  |  |
| 1.317 | The Contractor shall allow for the submission of samples of components and materials used in the construction works for the approval of the Project Manager in order that the Project Manager can satisfy himself of their construction or quality and that they meet the requirements of the Employer and, where applicable, any relevant authority. The Contractor shall also upon request prepare sample panels on the site to enable the Project Manager to judge the effect of the materials in the position which they will be used. Each sample shall be labelled as to origin and intended use in the works. The Project Manager shall have the right to reject any material or workmanship not in conformity with the approved samples. | Sum | 1 |  |  |  |
| 1.318 | Opening Up of Work | - | 0 |  |  |  |
| 1.319 | The Contractor shall provide for the opening up of any work for inspection, or the testing of any work, materials or goods (including making good afterwards). No claims will be entertained where such inspection or testing reveals a breach of contract by the Contractor. | Sum | 1 |  |  |  |
| 1.320 | Advertisements, Notices, etc | - | 0 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 1.321 | No advertisements, notices and the likes shall be allowed on any part of the construction works including hoardings, fencings, etc | Sum | 1 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1.322 | Quality Control | - | 0 |  |  |  |
| 1.323 | The Contractor shall allow for the setting up of a quality assurance system for the whole duration of the construction works to the approval of the Project Manager. Compliance with the quality assurance system shall not relieve the Contractor of his duties, obligations or responsibilities under the contract. | Sum | 1 |  |  |  |
| 1.324 | Maintenance Manuals | - | 0 |  |  |  |
| 1.325 | The Contractor shall allow for the provision of maintenance manuals to the Project Manager on completion of the works including any other technical documents required by the Project Manager. | Sum | 1 |  |  |  |
| 1.326 | Bar Bending Schedules | - | 0 |  |  |  |
| 1.327 | The Contractor shall allow here for the submission of bar bending schedules measured from Engineer's drawings all in acordance with BS4466 (1969) and to the approval of the Engineer. The Contractor shall submit copies of approved bar bending schedules to the Quantity Surveyor for the purpose of valuations and Final Account. | Sum | 1 |  |  |  |
| 1.328 | Key Site Personnel and Technical Personnel Required | - | 0 |  |  |  |
| 1.329 | The Contractor shall allow for all costs associated with the provision of key site personnel and Technical Personnel required for the works. | - | 0 |  |  |  |
| 1.330 | One Contract Manager as referred to Section 1-Instruction to Bidders Section 10(c ).The duties of the Contract Manager shall be amongst others to attend site meetings,coordination meetings and site visits. | Sum | 1 |  |  |  |
| 1.331 | One site agent on site on a full time basis with a minimum of 5 years relevant experience and holding at least a Diploma in Building and Civil Engineering or any similar qualification from a recognised institution.The site agent shall be full time on site | Sum | 1 |  |  |  |
| 1.332 | One Quantity Surveying Technician with minimum 5 years` relevant experience holding at least a Diploma in Quantity Surveying or a similar qualification. | Sum | 1 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 1.333 | One registered Electrical Engineer with a minimum of 5 years post registration experience | Sum | 1 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1.334 | One registered Mechanical Engineer with a minimum of 3 years post registration experience in Building services. The duties of the Mechanical Engineer shall be amongst others to attend site meetings,coordination meetings and site visits. | Sum | 1 |  |  |  |
| 1.335 | One General Foreman with minimum 10 years` relevant experience.The General Foreman shall be full time on site. | Sum | 1 |  |  |  |
| 1.336 | One Electrical Technician (NQF Level 4) with minimum 5 years` experience holding:(a) Level 3 IV Q Advanced Diploma in Electrical Installation (City & Guilds of London Institute)or (b)Level 3 Diploma in Engineering-Electrical & Electronic Engineering (City & Guilds of London Institute)or (c )NC Level 4 in Electrical Installation Works (MITD/MES) or (d)NTC Level 2 vin Electrical Installation Works (MITD/MES) or any other qualification to the above. | Sum | 1 |  |  |  |
| 1.337 | At least one experienced Electrician holding :(a)NTC Level 3 in Electrical Installation works (MITD/;MES) or (b)NC Level 3 in Electrical Installation works(MITD/MES) OR (c )Level 2 Certificate in Engineering-Electrical & Electronics Technology(City & Guilds of London Institute) or (d)any other alternative qualification to the above. | Sum | 1 |  |  |  |
| 1.338 | One Plumbing Technician (NQF Level 4) with minimum 5 years experience holding: (a)Level 3 IVQ Advanced Diploma in Plumbing (City & Guilds of London Institute) or (b)NC Level 4 in Plumbing (MITD/MES) or any other alternative qualification to the above. | Sum | 1 |  |  |  |
| 1.339 | One Health and Safety Officer | Sum | 1 |  |  |  |
| 1.340 | Special Note on Demobilisation | - | 0 |  |  |  |
| 1.341 | Contractor to allow for the cleaning of the site, the building and making good to any access road used during construction. | Sum | 1 |  |  |  |
|  | Total carried to summary sheet |  |  |  |  |  |

| NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Item Number | Description | Unit of Measure | QTY | Rate | Amount |  |
|  |  |  |  |  | Rs | Cs |
| 2.0 | BILL NO. 2 - DEMOLITION WORKS | - | 0 |  |  |  |
| 2.1 | ADMEASUREMENT | - | 0 |  |  |  |
| 2.2 | General notes | - | 0 |  |  |  |
| 2.3 | The contractor is advised to visit the site prior to submission of his bid. Demolition works comprise of the demolition of items as specified, all as per Architect’s Instructions. These items shall be counter checked by the Ministry of National Infrastructure‘s representative at their respective stores. Contractor to allow for the protection of existing structures and shall be required to make good as per the Architect’s Requirements if any structure is damaged during the demolition or dismantling works. | - | 0 |  |  |  |
| 2.4 | Contractor shall take all necessary precautions to keep these areas in tidy conditions, free from dust and minimum noise during the demolition works. | - | 0 |  |  |  |
| 2.5 | All salvage/-re-usable materials shall become the property of the Employer unless otherwise specified and transported to the nearest store of the Ministry of National Infrastructure as directed by the Project Manager. All usable materials arising from demolition shall be removed and disposed from site. The contractor shall have to keep a diary to record all salvaged materials to be handed over to the Employer which shall be checked and signed by the Employer’s agent. | - | 0 |  |  |  |
| 2.6 | General Site | - | 0 |  |  |  |
| 2.7 | Demolish concrete kerbs of approximate length 85 metres and cart away | Item | 1 |  |  |  |
| 2.8 | Demolish low wall and fencing of approximate length 100 metres and cart away | Item | 1 |  |  |  |
| 2.9 | Demolish concrete steps of approximate length 15 metres and cart away | Item | 1 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 2.10 | Remove existing doors of average size 2600mm to 4000mm wide and hand over to client | No | 3 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 2.11 | Demolish existing flower boxes of approximate length 15 metres by 1 metre wide up to foundation level, include for grubbing up foundation and disposal of unenviable material as directed by the Architect/ Engineer in charge arising from demolition as per Demolition Plan. | Item | 1 |  |  |  |
| 2.12 | Remove existing garbage bin and hand over to client | No | 1 |  |  |  |
| 2.13 | Remove existing concrete debris and replace by grass planting including topsoil to the approval of the Architect and Engineer. | Item | 1 |  |  |  |
| 2.14 | Remove existing interlocking blocks of approximate area 35 square metres and hand over to client | Item | 1 |  |  |  |
| 2.15 | Demolish existing absorption pit 4200 mm x 2900 mm and cart away | No | 1 |  |  |  |
| 2.16 | Demolish part of existing boundary wall of approximate length 3 metres so as to provide access to the new garbage bin and cart away | Item | 1 |  |  |  |
| 2.17 | Make good front boundary wall of approximate length 2650mm to the approval of the Architect/Engineer | Item | 1 |  |  |  |
| 2.18 | Remove all existing movable furniture and re-usable items including fencing and hand over to client | Item | 1 |  |  |  |
| 2.19 | Make good to any existing damaged rendering,structure or any damage caused to existing structure,equipment,materials during demolition works under the supervision and approval of the Architect and Engineer. | Item | 1 |  |  |  |
| 2.20 | Allow for protection and /or deviation of services (electrical,mechanical etc) underground or above that may run on site under the supervision of the Mechanical and Electrical Engineer. | Item | 1 |  |  |  |
|  | Total carried to summary sheet |  |  |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| ITEM NO | DESCRIPTION | Unit of Measure | QTY | Rate | Amount |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Rs | Cs |
| 3.1 | BILL NO. 3 - COMMUNITY WELLNESS CENTRE | - | 0 |  |  |  |
| 3.2 | ADMEASUREMENT | - | 0 |  |  |  |
| 3.3 | SECTION 1 - SUBSTRUCTURE | - | 0 |  |  |  |
| 3.4 | EXCAVATION AND EARTHWORK | - | 0 |  |  |  |
| 3.5 | Excavation works shall be deemed to include excavation in all types of materials including rock strata, and working space allowance wherever required. Earthwork support and keeping excavation free from ground and surface water are also deemed to be included in measured items for excavation. | - | 0 |  |  |  |
| 3.6 | Excavate, starting from stripped level, trenches to receive foundations and deposite in temporary spoil heaps on site. | m3 | 144 |  |  |  |
| 3.7 | Excavate starting from stripped level, pits to receive column bases and deposite in temporary spoil heaps on site. | m3 | 204 |  |  |  |
| 3.8 | Excavating soft spot or fill material including earthwork support below excavations to bases or trenches and remove from site. | m3 | 10 |  |  |  |
| 3.9 | Disposal | - | 0 |  |  |  |
| 3.10 | Excavated material | - | 0 |  |  |  |
| 3.11 | Backfilling to sides of trenches and bases Selected execavated materials from spoil heaps, deposited and compacting in layers n.e. 200 mm in backfilling to excavations to engineer's specifications | m3 | 205 |  |  |  |
| 3.12 | Carting away Haul up from spoil heaps and remove surplus excavated material from site to suitable tip. | m3 | 143 |  |  |  |
| 3.13 | Imported Filling | - | 0 |  |  |  |
| 3.14 | Clean dry non-expansive selected fill to Engineer`s approval and compacted to specifications | m3 | 70 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 3.15 | Imported filling Hardcore filling composed of good hard stones ballast n.e. 150 mm in size , depositing and compacting in layers n.e. 225 mm thick to engineer's specifications in filling to make up levels under floors | m3 | 145 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 3.16 | Crusher run 0-20, 100 mm thick layer, laid on hardcore (m/s) compacted to 95% BS Heavy to specifications | m3 | 30 |  |  |  |
| 3.17 | Rocksand, 25 mm thick layer, well watered and compacted to specifications to receive polythene sheeting (m/s) | m3 | 8 |  |  |  |
| 3.18 | Surface Treatment | - | 0 |  |  |  |
| 3.19 | Level and compact bottom of excavations to 95% BS Heavy | - | 0 |  |  |  |
| 3.20 | Bases | m2 | 102 |  |  |  |
| 3.21 | Strip footing | m2 | 72 |  |  |  |
| 3.22 | Subgrade | m2 | 290 |  |  |  |
| 3.23 | Sundries in excavations | - | 0 |  |  |  |
| 3.24 | Polythene sheeting, 0.23mm thick in single layer, laid under floor bed with 150mm laps to receive concrete (measured net-no allowance for laps) | m2 | 335 |  |  |  |
| 3.25 | Saturate with anti-termite treatment or approved equivalent soil below floor bed and to perimeter facade of substructure. The works shall be done by an approved specialist and latter shall provide a decennial warranty for the treatment works. The contractor shall submit a detailed methodology of proposed treatment and products to be approved by Architect prior to start of work.(Approximate building footprint 302 m2 and 96 m to perimeter) | Item | 1 |  |  |  |
| 3.26 | Allow for all temporary support incidental to demolitions and excavations including shoring and scaffolding and making good all work disturbed. | Item | 1 |  |  |  |
| 3.27 | Allow for keeping all excavations free from all water, mud and the like by pumping, bailing or other means including the provision of all necessary pumps, temporary plumbing, etc. | Item | 1 |  |  |  |
| 3.28 | CONCRETE WORK | - | 0 |  |  |  |
| 3.29 | Plain in-situ concrete, designed mix Grade 15 N/mm², 40 mm aggregate, as described in | - | 0 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 3.30 | Blinding layer, 50 mm thick under bases, foundations and the like | m3 | 11 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 3.31 | Reinforced in-situ concrete designed mix Grade 30 N/mm², as described in | - | 0 |  |  |  |
| 3.32 | Foundations in trenches cast against faces of excavation | m3 | 18 |  |  |  |
| 3.33 | Column bases cast against faces of excavation | m3 | 45 |  |  |  |
| 3.34 | Columns | m3 | 13 |  |  |  |
| 3.35 | Tie columns | m3 | 3 |  |  |  |
| 3.36 | RC wall to staircase | m3 | 1 |  |  |  |
| 3.37 | Ground Beam | m3 | 25 |  |  |  |
| 3.38 | Surface bed including thickening, 115mm thick | m3 | 35 |  |  |  |
| 3.39 | Mild steel reinforcement to MS 10 hot rolled plain round mild steel to concrete members generally. | - | 0 |  |  |  |
| 3.40 | 6mm Diameter Bars | Kg | 2500 |  |  |  |
| 3.41 | High tensile steel reinforcement to MS 10 hot rolled high yield steel to concrete members generally, | - | 0 |  |  |  |
| 3.42 | bars of various diameter | Kg | 10500 |  |  |  |
| 3.43 | Fabric reinforcement to MS 34 & MS35 laid with side and end laps to concrete members generally, | - | 0 |  |  |  |
| 3.44 | Mesh reinforcement type A142 (2.22kg/m) | m2 | 335 |  |  |  |
| 3.45 | Formwork in class 2 finish, strutting at/from any level and including rebates or groove formers, as described to | - | 0 |  |  |  |
| 3.46 | Sides of columns | m2 | 185 |  |  |  |
| 3.47 | Sides of tie columns | m2 | 35 |  |  |  |
| 3.48 | Sides of Ground Beam | m2 | 250 |  |  |  |
| 3.49 | Sides of RC wall to staircase | m2 | 5 |  |  |  |
| 3.50 | Edges of surface bed | m | 95 |  |  |  |
| 3.51 | CONCRETE SUNDRIES | - | 0 |  |  |  |
| 3.52 | Induced Joints | - | 0 |  |  |  |
| 3.53 | Groove 20mm deep by 6mm wide to be cut in ground floor slab within 48 hrs after concreting floor slab. Induced joints to be at the locations shown in drawings or as instructed by Structural Engineer, all as described in Engineer's specifications. | Item | 1 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 3.54 | BLOCKWORK AND STONEWORK | - | 0 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 3.55 | Hollow concrete blockwalling to BS 6073 Grade A with a minimum average compressive strength of 3.5 N/mm², laid in cement and rocksand (1:3) mortar with an approved plasticiser as specified. Rate to include for wall ties all as described in Engineer's specifications: | - | 0 |  |  |  |
| 3.56 | 200mm thick wall | m2 | 380 |  |  |  |
| 3.57 | 150mm thick wall | m2 | 85 |  |  |  |
| 3.58 | FINISHES EXTERNALLY | - | 0 |  |  |  |
| 3.59 | Cement and sand (1:3) render, 20mm thick in two coats mixed with an approved plasticiser on the following surfaces including preparation of surfaces. Rate shall include for hacking and labour for forming arises and fair edges , sponge finish externally on: | - | 0 |  |  |  |
| 3.60 | Walls, returns, reveals and the like | m2 | 50 |  |  |  |
| 3.61 | DECORATION EXTERNALLY | - | 0 |  |  |  |
| 3.62 | Prepare and apply one coat undercoat and two coats of anti-fungus water repellant paint of an approved colour on the following rendered surfaces:- (5 Years Guarantee to be provided) | - | 0 |  |  |  |
| 3.63 | walls, returns, reveals and the like | m2 | 50 |  |  |  |
| 3.64 | SECTION 2 - SUPERSTRUCTURE | - | 0 |  |  |  |
| 3.65 | CONCRETE WORKS | - | 0 |  |  |  |
| 3.66 | Reinforced in-situ concrete, Grade 20 N/mm², as described, in | - | 0 |  |  |  |
| 3.67 | cills, lintels and the like | m3 | 5 |  |  |  |
| 3.68 | Reinforced in-situ concrete, Grade 30 N/mm², as described, in | - | 0 |  |  |  |
| 3.69 | suspended slab n.e 150mm thick | m3 | 42 |  |  |  |
| 3.70 | Landings | m3 | 1 |  |  |  |
| 3.71 | Columns | m3 | 28 |  |  |  |
| 3.72 | Tie Columns | m3 | 5 |  |  |  |
| 3.73 | Downstand beams | m3 | 35 |  |  |  |
| 3.74 | Staircases | m3 | 3 |  |  |  |
| 3.75 | Coping to parapet wall | m3 | 6 |  |  |  |
| 3.76 | Mild steel reinforcement to MS 10 hot rolled plain round mild steel to concrete members generally, | - | 0 |  |  |  |
| 3.77 | 6mm Diameter Bars | kg | 3800 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 3.78 | High tensile steel reinforcement to MS 10 hot rolled high yield steel to concrete members generally, | - | 0 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 3.79 | bars of various diameters | kg | 15200 |  |  |  |
| 3.80 | Formwork in class 2 finish, strutting at/from any level and including rebates or groove formers, as described to | - | 0 |  |  |  |
| 3.81 | soffit of slab 150mm thick | m2 | 274 |  |  |  |
| 3.82 | Soffit of landings 175mm thick | m2 | 4 |  |  |  |
| 3.83 | Slopping Soffit of staircase | m2 | 11 |  |  |  |
| 3.84 | sides and soffit of downstand beams | m2 | 290 |  |  |  |
| 3.85 | sides and soffit of cills, lintels and the like | m2 | 25 |  |  |  |
| 3.86 | sides of columns and tie columns | m2 | 360 |  |  |  |
| 3.87 | Sides of coping to parapet wall | m2 | 35 |  |  |  |
| 3.88 | Edges of staircases, extreme 250-500mm high | m | 10 |  |  |  |
| 3.89 | Edges of risers n.e 250mm high | m | 30 |  |  |  |
| 3.90 | Edges of slab n.e 150mm high | m | 91 |  |  |  |
| 3.91 | SECTION 3 - BLOCK AND STONEWALLING | - | 0 |  |  |  |
| 3.92 | Hollow concrete blockwalling to BS 6073 Grade A with a minimum average compressive strength 3.5 N/mm² laid in cement and rocksand (1:3) mortar with an approved plasticiser as specified. Rate to include for filling of voids at door and window jambs with concrete grade 15N/mm2, reinforcement as specified and wall ties as specified, all as described in Engineer's specifications in: | - | 0 |  |  |  |
| 3.93 | Blockwalling | - | 0 |  |  |  |
| 3.94 | 200mm thick | m2 | 401 |  |  |  |
| 3.95 | 150mm thick | m2 | 30 |  |  |  |
| 3.96 | 100mm thick | m2 | 25 |  |  |  |
| 3.97 | SECTION 4 - METALWORK | - | 0 |  |  |  |
| 3.98 | STAINLESS STEEL HANDRAILS | - | 0 |  |  |  |
| 3.99 | Stainless steel handrails in hollow sections including steel plates, bolts, ends, joints, cuts, angles, intersections, stopped ends and the like. Works include for welding, cutting and fixing. | - | 0 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 3.100 | Stainless steel handrails(Grade 316) overall height 1000mm comprising of 50x20mm RHS stainless steel,40mm diameter CHS stainless steel and 20mm diameter stainless steel rod and 50mm diameter CHS stainless steel fixed to 75x75mm stainless steel plate complete with all finishes to stainless steel handrails to the satisfaction and approval of the Architect and Engineer all as per Drg No G859/11 | m | 10 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 3.101 | Stainless steel handrail (Grade 316) comprising of 40mm diameter stainless steel tube welded to 12mm diameter stainless steel rod fixed to wall with metal plate complete with all finishes to the satisfaction and approval of the Architect and Engineer all as per drawings No. G859/11 | m | 14 |  |  |  |
| 3.102 | SECTION 5 - ROOF STRUCTURES AND ROOF COVERINGS | - | 0 |  |  |  |
| 3.103 | EXTERNAL WORK TO CONCRETE BASE | - | 0 |  |  |  |
| 3.104 | Cement and sand (1:3) screed mixed with an approved waterproofing compound in strict accordance with manufacturer's specifications to the following concrete surfaces. Rate shall include for all necessary preparation of surfaces, hacking of concrete and labour for forming arrises and fair edges. Screed shall be laid to falls and crossfalls and dished towards outlets. Finishes to screed and rendering including slope and wherever required shall be finished to the satisfaction and approval of the waterproofing contractor/ specialist and to the approval of the Architect and Engineer. A signed statement shall be submitted by the waterproofing Contractor for approval of the above work. | - | 0 |  |  |  |
| 3.105 | 25 mm thick average screed laid to falls and crossfalls including to flat roofs including 50x50mm haunching at corners to receive waterproofing | m2 | 274 |  |  |  |
| 3.106 | Cement plaster (1:3) render with a smooth trowelled finish as described to receive waterproofing membrane | - | 0 |  |  |  |
| 3.107 | 25mm thick render to sides and top of upstands and parapet walls. | m2 | 55 |  |  |  |
| 3.108 | ROOF WATERPROOFING AND FLASHING | - | 0 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 3.109 | Supply and lay approved double layer bituminous waterproofing membrane by a specialist in strict accordance to manufacturer's specifications and as described (10 years guarantee to be given) | - | 0 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 3.110 | Waterproofing membrane on screeded flat roof slab including working around rainwater heads (measured nett) | m2 | 274 |  |  |  |
| 3.111 | Dressing up sides and top of upstands including over tilting filet, tucking into including forming groove in wall and cement mortar | m2 | 55 |  |  |  |
| 3.112 | Aluminium flashing | - | 0 |  |  |  |
| 3.113 | Provide and fix in position shaped aluminium flashing with approved quality rust proof screws on concrete and block surfaces. Rate to include for silicon sealant or equivalent to manufacturer's specification, cutting, lapping, bending, edge, tucking in grooved all as per Architect's drawings | - | 0 |  |  |  |
| 3.114 | 200mm girth, bend-2 | m | 105 |  |  |  |
| 3.115 | Rainwater pipes and accessories | - | 0 |  |  |  |
| 3.116 | Rigid UPVC pressure pipes type PN16 rainwater pipes to comply to BS or other approved standard with solvent welded joints cast in concrete or fixed on surface with and including bends,elbows,tees and standard brackets, plugged to concrete | - | 0 |  |  |  |
| 3.117 | 110mm diameter pressure type UPVC PN16 rainwater downpipe | m | 30 |  |  |  |
| 3.118 | Roof outlet to suit 110mm diameter pipe laid horizontally with stainless steel wire balloon grating | No. | 6 |  |  |  |
| 3.119 | High quality inox 316 stainless steel wire balloon | No. | 6 |  |  |  |
| 3.120 | Good quality fibre glass gargoyle to Architect and Engineer approval and fixed to RC structure as per manufacturer`s specifications | No. | 6 |  |  |  |
| 3.121 | Prepare and apply one coat of undercoat and two coats of anti-fungus finishing coats of emulsion paint on the following surfaces paint. BS colour to Architect's approval to | - | 0 |  |  |  |
| 3.122 | Anti-fungus paint on surfaces of 110mm diameter exposed PVC pipes and bends | m | 30 |  |  |  |
| 3.123 | SECTION 6 - DOORS AND WINDOWS | - | 0 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 3.124 | POWDER COATED ALUMINIUM OPENINGS | - | 0 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 3.125 | The following Aluminium openings shall be aluminium alloy 6060 A.G.S and shall be to BS EN 1192 and BS EN 1529 regarding height, width, thickness and squareness or as per manufacturer's specifications. Resistance to windload shall be to BS EN 12210 and to withstand cyclonic winds as per current wind gusts pressure over 280km/hr substantiated with calculations and certificates as required and to the approval of the Engineer. Aluminium openings shall be powder coated (colour to Architect's approval) and shall be supplied with all hinges, knobs, handles, etc. as required. Thickness of aluminium section to be of minimum 2mm. Opening to be water and air tight to be BS 16375 Part 1 Class A. Handle and Lock to be BS 6093 part 1. Gasket (E.P.D.M) to BS4255 part 1.Opening to assembly to BS6093 and glazing to be 6262. Glazing shall be laminated glass of minimum thickness 8.38mm. Corned cleat any other reinforcement to be used must be of same aluminium mat. All handle lock to aluminium doors, windows and duct doors to be of cremone type.Standard overhead self closing device unit(Automatic door closer) one per leaf to meet BS 6459:door closers and accessories should comply fully with BSEN1154.Master key to be provided. A warranty of minimum 5 years to be submitted by contractor on all aluminium handles and fittings. Fixation details including (locks, compass, etc.) to be approved by Architect & Engineer. | - | 0 |  |  |  |
| 3.126 | Doors | - | 0 |  |  |  |
| 3.127 | Sliding/Folding door | - | 0 |  |  |  |
| 3.128 | Door Ref; D1 overall size 5400 x 2400 mm high | No. | 1 |  |  |  |
| 3.129 | Door Ref; D1 overall size 5475 x 2400 mm high | No. | 1 |  |  |  |
| 3.130 | Corner Sliding door | - | 0 |  |  |  |
| 3.131 | Door Ref. D3 overall size 4700 x 2400 mm high | No. | 1 |  |  |  |
| 3.132 | Single leaf full panelled door | - | 0 |  |  |  |
| 3.133 | Door Ref. D6 overall size 1000 x 2100 mm high | No. | 1 |  |  |  |
| 3.134 | Single leaf full panelled door | - | 0 |  |  |  |
| 3.135 | Door Ref. D8 overall size 900 x 2100 mm high | No. | 3 |  |  |  |
| 3.136 | Single leaf full panelled door | - | 0 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 3.137 | Door Ref. D9 overall size 800 x 2100 mm high | No. | 4 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 3.138 | Single leaf full panelled door | - | 0 |  |  |  |
| 3.139 | Door Ref. D10 overall size 900 x 1950 mm high | No. | 1 |  |  |  |
| 3.140 | Windows | - | 0 |  |  |  |
| 3.141 | Window Ref; W1 overall size 2425 x 2200mm high | No. | 2 |  |  |  |
| 3.142 | Window Ref; W2 overall size 3050 x 1900mm high | No. | 1 |  |  |  |
| 3.143 | Window Ref; W3 overall size 1500 x 1900mm high | No. | 1 |  |  |  |
| 3.144 | Window Ref; W4 overall size 1500 x 1300mm high | No. | 1 |  |  |  |
| 3.145 | Window Ref; W5 overall size 500 x 3000mm high | No. | 2 |  |  |  |
| 3.146 | Window Ref; W6 overall size600 x1200mm high | No. | 1 |  |  |  |
| 3.147 | Top Light Ref; TL1 overall size 5550 x 800mm high | No. | 2 |  |  |  |
| 3.148 | Top Light Ref; TL2 overall size 600 x 600mm high | No. | 4 |  |  |  |
| 3.149 | Aluminium Skylight | - | 0 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 3.150 | The following Aluminium skylight shall be of aluminium alloy 6060 A.G.S and shall be to BS EN 1192 and BS EN 1529 regarding height,width,thickness and squareness or as per manufacturer`s specifications.For water tightness and air tightness openings shall comply to BS EN 12207 or BS EN 12208.Resistance to wind load shall be to BS EN 12210 and to withstand cyclonic winds as per current wind gusts pressure over 280km/hr substantiated with calculations and certificates as required and to the approval of the Engineer.Anodisation shall be to EWAA-Euras class 20 and shall be supplied with all hinges,knobs,handles etc as required.Aluminium skylight to be water tight air tight BS 16375 Part 1 Class A.All dimensions on this drawing to be confirmed on site prior to manufacturing.Aluminium skylight to BS 4255 Part 1.Aluminium skylight to assembly to BS 6093 &Glazing to BS 6262.Corner cleat any other reinforcement to be used must be of same aluminium material.10 mm laminated clear glazing fixed to Aluminium ,Aluminium flashing to be provided and 75 mm PVC gutter fixed to aluminium all as per Architect and Engineer approval.500x100x15mm treated Balao wood varnished color to Architect`s approval and fixation system to Architect and Engineer approval all as per Drwg No G859/14.Contractor to provide shop drawings for fixation and assemblage system to be approved by the Architect and Engineer prior to manufacturing.Water test to be carried out by the contractor to the satisfaction of the representative of the MNI&CD. | - | 0 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 3.151 | Aluminium Skylight overall size 4540mmx2940mm (measured flat) | No. | 1 |  |  |  |
| 3.152 | BURGLAR BARS | - | 0 |  |  |  |
| 3.153 | Supply and Fixing of Burglar Proofing to windows/vents comprising of 16mm diameter galvanised solid metal rods fixed to galvanised metal plate 40x8mm thick. Burglar proofing to be hot-dipped galvanised after manufacture. Fixation points (4 Nos) of burglar proofing to be 75mm anchored in R.C jamb of window with epidermix A372 or approved equivalent.Rate to include all welding, fixing, fittings, accessories and finishes to Architect's Approval and as per drawing No G859/10 | - | 0 |  |  |  |
| 3.154 | to fit opening | - | 0 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 3.155 | overall size 2400 x 2200mm high | No. | 2 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 3.156 | overall size(1300 +1500)x1900 mm high | No. | 1 |  |  |  |
| 3.157 | overall size 1500 x 1900mm high | No. | 1 |  |  |  |
| 3.158 | overall size 1500 x 1300mm high | No. | 1 |  |  |  |
| 3.159 | overall size 5550 x 800mm high | No. | 2 |  |  |  |
| 3.160 | overall size 600 x 600mm high | No. | 4 |  |  |  |
| 3.161 | overall size 600x1200mm high | No. | 1 |  |  |  |
| 3.162 | overall size 500x3000mm high | No. | 2 |  |  |  |
| 3.163 | Prepare surface, treat with etch primer and paint with one coat of super galva primer, two coats hard gloss enamel paint,colour to Architect`s approval on the following surfaces | - | 0 |  |  |  |
| 3.164 | Burglar bars to windows and vents (measured flat both sides) | m2 | 70 |  |  |  |
| 3.165 | COLLAPSIBLE GRILLS | - | 0 |  |  |  |
| 3.166 | Aluminium collapsible side hung door;colour to Architect`s approval complete with top and botom rails and approved locking system | - | 0 |  |  |  |
| 3.167 | overall size 5400x2400mm | No. | 1 |  |  |  |
| 3.168 | overall size 5475x2400mm | No. | 1 |  |  |  |
| 3.169 | overall size 2200x3000mm | No. | 1 |  |  |  |
| 3.170 | overall size 4700x2400mm | No. | 1 |  |  |  |
| 3.171 | TIMBER DOORS | - | 0 |  |  |  |
| 3.172 | The following Timber double leaves door as per Architect`s drawing.Door shall be supplied with 2 pairs of heavy duty stainless steel hinges to BS 7352 class 5-Fire Resistance to BS .3 lever mortice sash lock to BS 4951 heavy duty category.2 pairs of heavy duty stainless steel handle Grade 316 in both sides of the door and automatic door closer.Fixation details to be approved by Architect & Engineer. Door to be finished with 1 coat wood primer and 2 coats varnish to Architect`s approval and as per drawings. | - | 0 |  |  |  |
| 3.173 | Double leaf full panelled door | - | 0 |  |  |  |
| 3.174 | Door Ref. D2 overall size 2200 x 3000 mm high | No. | 1 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 3.175 | The following Timber single leaf door as per Architect`s drawing.Door shall be supplied with one and a half pair of heavy duty brass butt hinges to BS 7352 class 5-Fire Resistance to BS 476 Part 22,3 lever mortice sash lock to BS 4951 heavy duty category .Heavy duty anodised aluminium tubular handle to BS 4951 category .Kick and push plate silver anodised 1.2 mm thick 200 mm wide on both sides BS 2911 and automatic door closer.Fixation details to be approved by Architect & Engineer. Door to be finished with 1 coat wood primer and 2 coats acrylic paint spray applied enamel to Architect`s approval and as per drawings | - | 0 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 3.176 | Single leaf full panelled door | - | 0 |  |  |  |
| 3.177 | Door Ref. D7 overall size 900 x 2100 mm high | No. | 1 |  |  |  |
| 3.178 | The following Timber double leaves door as per Architect`s drawing.Door shall be supplied with one and a half pair of heavy duty brass butt hinges to BS 7352 class 5-Fire Resistance to BS 476 Part 22,3 lever mortice sash lock to BS 4951 heavy duty category.Heavy duty anodised aluminium tubular handle to BS 4951 category .Kick and push plate silver anodised 1.2 mm thick 200 mm wide on both sides BS 2911 and automatic door closer.Fixation details to be approved by Architect & Engineer. Door to be finished with 1 coat wood primer and 2 coats acrylic paint spray applied enamel to Architect`s approval and as per drawings | - | 0 |  |  |  |
| 3.179 | Double leaf full panelled door | - | 0 |  |  |  |
| 3.180 | Door Ref. D4 overall size 1200 x 2100 mm high | No. | 1 |  |  |  |
| 3.181 | The following balaoTimber single leaf 2100 mm door in varnished treated timber balao with lock and 1700mm varnished treated balao timber wood cladding (fix) as per Architect`s drawing.Door shall be supplied with one and a half pair of heavy duty brass butt hinges to BS 7352 class 5-Fire Resistance to BS 476 Part 22,3 lever mortice sash lock to BS 4951 heavy duty category 2.Heavy duty anodised aluminium tubular handle to BS 4951 category 1.Fixation details to be approved by Architect & Engineer. Door to be finished with 1 coat wood primer and 2 coats varnish to Architect`s approval and as per drawings. | - | 0 |  |  |  |
| 3.182 | Single leaf full panelled door | - | 0 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 3.183 | Door Ref. D11 overall size 800 x 2100 mm high | No. | 1 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 3.184 | METAL DOOR | - | 0 |  |  |  |
| 3.185 | The following emergency fire exit single leaf door as per Architect`s drawing.Steel fire exit door shall be supplied with 2 pair single axis hinges to be BS EN 1935:2002 and should be tested as part of the door set to BS EN 1634-2.Dimension of hinges to be as per manufacturer`s specifications.Lock and latch-to BS EN 12209:2003 panic bolt push bar to manufacturer`s specifications and overhead door closer surface mounted to BS EN 1154:1997.Thickness of door leaf to be min 48mm as per manufacturer`s specifications.Door to be panelled with zinc coated mild steel sheet 1.2 mm thick fire resistance up to 60 minutes with durable powder coat finish to manufacturer`s specifications and to the approval of the Architect and as per drawings. | - | 0 |  |  |  |
| 3.186 | Single leaf full panelled door | - | 0 |  |  |  |
| 3.187 | Door Ref. D5 overall size 900 x 2100 mm high | No. | 1 |  |  |  |
| 3.188 | Glass Blocks | - | 0 |  |  |  |
| 3.189 | Glass block 200x 200x 100 mm thick.Sample,specs and colour to Architect`s approval.Fixation of glass block including silicon mastic pointing to perimeter internally and externally and the like to Architect`s and Engineer`s approval | - | 0 |  |  |  |
| 3.190 | GB1- overall size 415x1060mm | No | 1 |  |  |  |
| 3.191 | SECTION 7- FINISHES | - | 0 |  |  |  |
| 3.192 | INTERNAL WORK TO BLOCKWORK OR CONCRETE BASE | - | 0 |  |  |  |
| 3.193 | Floor finishes | - | 0 |  |  |  |
| 3.194 | Internal Floor Finishes | - | 0 |  |  |  |
| 3.195 | Cement and sand (1:3) as specified laid on concrete surfaces including preparation of surfaces. Rate shall include for forming arises and fair edges etc. | - | 0 |  |  |  |
| 3.196 | 25mm thick screed laid to receive ceramic tiles | - | 0 |  |  |  |
| 3.197 | Floors and landing laid level | m2 | 225 |  |  |  |
| 3.198 | Treads | m2 | 10 |  |  |  |
| 3.199 | Risers and edges of landings | m2 | 6 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 3.200 | Supply and lay heavy duty non skid homogenous ceramic tiles as described on screeded backing (elsewhere measured). Ceramic tiles shall conform to the requirements of ISO 13006 or EN176(SC R10) standards Colour and pattern to Architect's approval. Rate shall include for any necessary cutting, fittings, approved floor tile backing adhesive strictly applied in accordance with manufacturer's instructions and including 2mm joints or other approved thickness flush pointed with an approved coloured waterproof grout to Architect's approval,vee groove to joint of tiles, labours and cleaning on completion. Samples shall be submitted to the Architect for approval prior of ordering and start of work. | - | 0 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 3.201 | Floors and landing laid level | - | 0 |  |  |  |
| 3.202 | Size 600x300 x10mm thick (R10) | m2 | 50 |  |  |  |
| 3.203 | Supply and lay heavy duty non skid homogenous ceramic tiles (Marble effect) as described on screeded backing (elsewhere measured). Ceramic tiles shall conform to the requirements of ISO 13006 (R10) or EN176 standards Colour and pattern to Architect's approval. Rate shall include for any necessary cutting, fittings, approved floor tile backing adhesive strictly applied in accordance with manufacturer's instructions and including 2mm joints or other approved thickness flush pointed with an approved coloured waterproof grout to Architect's approval,vee groove to joint of tiles, labours and cleaning on completion. Samples shall be submitted to the Architect for approval prior of ordering and start of work. | - | 0 |  |  |  |
| 3.204 | Floors and landing laid level | - | 0 |  |  |  |
| 3.205 | Size 600x600 x10mm thick (R10) | m2 | 45 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 3.206 | Supply and lay heavy duty polished non skid homogenous ceramic tiles (Marble effect) as described on screeded backing (elsewhere measured). Ceramic tiles shall conform to the requirements of ISO 13006 (R9) or EN176 standards Colour and pattern to Architect's approval. Rate shall include for any necessary cutting, fittings, approved floor tile backing adhesive strictly applied in accordance with manufacturer's instructions and including 2mm joints or other approved thickness flush pointed with an approved coloured waterproof grout to Architect's approval,vee groove to joint of tiles, labours and cleaning on completion. Samples shall be submitted to the Architect for approval prior of ordering and start of work. | - | 0 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 3.207 | Floors and landing laid level | - | 0 |  |  |  |
| 3.208 | Size 600x600 x10mm thick (R9) | m2 | 130 |  |  |  |
| 3.209 | Supply and lay vegetable soil with grass planting and plants to Architect`s approval + 800x400x50mm heavy duty concrete slabs. Colour and pattern to Architect's approval. Rate shall include for any necessary cutting, fittings, approved floor tile backing adhesive strictly applied in accordance with manufacturer's instructions and including 2mm joints or other approved thickness flush pointed with an approved coloured waterproof grout to Architect's approval, labours and cleaning on completion. Samples shall be submitted to the Architect for approval prior of ordering and start of work. | m2 | 12 |  |  |  |
| 3.210 | Supply and lay heavy duty non skid homogenous nosing granite as described on screeded backing (elsewhere measured). Nosing granite shall conform to the requirements of ISO 13006 (R10) or EN176 standards Colour and pattern to Architect's approval. Rate shall include for any necessary cutting, fittings, approved floor tile backing adhesive strictly applied in accordance with manufacturer's instructions and including 2mm joints or other approved thickness flush pointed with an approved coloured waterproof grout to Architect's approval, vee groove to joint of tiles,labours and cleaning on completion. Samples shall be submitted to the Architect for approval prior of ordering and start of work. | - | 0 |  |  |  |
| 3.211 | Treads | - | 0 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 3.212 | Nosing granite tiles size 320x20mm | m2 | 10 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 3.213 | Supply and lay 8mm thick traditional glazed ceramic spanish wall tiles as described on screeded backing (elsewhere measured). Ceramic wall tiles shall conform to the requirements of ISO 13006 or EN176(SC R10) standards Colour and pattern to Architect's approval. Rate shall include for any necessary cutting, fittings, approved floor tile backing adhesive strictly applied in accordance with manufacturer's instructions and including 2mm joints or other approved thickness flush pointed with an approved coloured waterproof grout to Architect's approval,vee groove to joint of tiles, labours and cleaning on completion. Samples shall be submitted to the Architect for approval prior of ordering and start of work. | - | 0 |  |  |  |
| 3.214 | Risers | - | 0 |  |  |  |
| 3.215 | Wall tiles 8mm thick | m2 | 6 |  |  |  |
| 3.216 | Skirting tiles size 600x150x10mm thick (R9) -100 mm high rounded edge homogenous ceramic tiles to EN 176 or ISO 13006 with anodised aluminium edging,matching floor tiles.Samples,specs and colour to Architect`s approval. | m | 100 |  |  |  |
| 3.217 | Wall finishes | - | 0 |  |  |  |
| 3.218 | Cement and sand (1:3) render 15mm thick mixed with an approved plasticiser on the following surfaces including preparation of surfaces. Rate shall include for hacking and labour for forming arises and fair edges , trowel smooth finish internally on: | - | 0 |  |  |  |
| 3.219 | walls, returns, reveals, columns, beams and the like | m2 | 520 |  |  |  |
| 3.220 | 15mm thick Cement Plaster (1:1:3) backing coat with wood floated finish, on the following surface. Rate shall include for hacking and labour for forming arises and fair edges, to receive ceramic wall tiling to: | - | 0 |  |  |  |
| 3.221 | walls, returns, reveals and the like | m2 | 90 |  |  |  |
| 3.222 | Supply and lay coloured glazed ceramic tiles as described, on rendered backing coat (elsewhere measured) with approved tile adhesive. Colour and pattern to Architect's approval. Ceramic tiles shall conform to the requirements | - | 0 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 3.223 | Ceramic wall tiles 600x300x10mm thick (to EN 177) glazed tiles with 2 mm wide joints or other approved width including pointing of joint with coloured waterproof grout to Architect's approval. Rate shall include for all necessary cutting, fittings, wastages, borders, labours and cleaning on completion. Samples,specs,colour and pattern to Architect`s approval.Wall tiles to be 2100mm high to all sides of internal walls with pvc edging to all vertical and horizontal edges.Samples shall be submitted to the Architect for approval prior of ordering and start of work. | - | 0 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 3.224 | walls, returns, reveals and the like | m2 | 90 |  |  |  |
| 3.225 | Ceiling finishes | - | 0 |  |  |  |
| 3.226 | Cement and sand (1:3) render 15mm thick mixed with an approved plasticiser on the following surfaces including preparation of surfaces. Rate shall include for hacking and labour for forming arises and fair edges, trowel smooth finish internally on: | - | 0 |  |  |  |
| 3.227 | Soffit of slabs and beams | m2 | 298 |  |  |  |
| 3.228 | Staircases | m2 | 20 |  |  |  |
| 3.229 | False ceilings | - | 0 |  |  |  |
| 3.230 | Supply and fix square perforated Aluminium ceiling panel 600x 600mm,thickness minimum 2mm,Derrick spacing 1000-1200mm.Aluminium sections to be powder coated,colour,design and pattern to Architect`s approval and fixation system and fire resistance to Engineer`s approval all as per Drwg No G859/16. Samples shall be submitted to the Architect for approval prior of ordering and start of work. | m2 | 175 |  |  |  |
| 3.231 | EXTERNAL WORK TO BLOCKWORK OR CONCRETE BASE | - | 0 |  |  |  |
| 3.232 | External Floor Finishes | - | 0 |  |  |  |
| 3.233 | Cement and sand (1:3) as specified laid on concrete surfaces including preparation of surfaces. Rate shall include for forming arises and fair edges etc. | - | 0 |  |  |  |
| 3.234 | 25 mm thick screed laid to receive ceramic tiles | - | 0 |  |  |  |
| 3.235 | Floors laid level | m2 | 45 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 3.236 | Supply and lay heavy duty non skid homogenous ceramic tiles (Marble effect) as described on screeded backing (elsewhere measured). Ceramic tiles shall conform to the requirements of ISO 13006 (R10) or EN176 standards Colour and pattern to Architect's approval. Rate shall include for any necessary cutting, fittings, approved floor tile backing adhesive strictly applied in accordance with manufacturer's instructions and including 2mm joints or other approved thickness flush pointed with an approved coloured waterproof grout to Architect's approval, labours and cleaning on completion. Samples shall be submitted to the Architect for approval prior of ordering and start of work. | - | 0 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 3.237 | Floors laid level | - | 0 |  |  |  |
| 3.238 | Size 600x600x10mm thick (R10) | m2 | 45 |  |  |  |
| 3.239 | External Wall finishes | - | 0 |  |  |  |
| 3.240 | Cement and sand (1:3) render 20mm thick in 2 coats mixed with an approved plasticiser on the following surfaces including preparation of surfaces to the approval of the Architect and as per Schedule of finishes and Drawings. Rate shall include for hacking and labour for forming arises and fair edges , sponge finish externally on: | - | 0 |  |  |  |
| 3.241 | walls, returns, reveals, beams, columns, and the like | m2 | 375 |  |  |  |
| 3.242 | Cement and sand (1:3) render 20mm thick in 2 coats mixed with an approved plasticiser on the following surfaces including preparation of surfaces to the approval of the Architect and as per Schedule of finishes and Drawings. Rate shall include for hacking and labour for forming arises and fair edges , rustic texture vertical finish externally on: | - | 0 |  |  |  |
| 3.243 | walls, returns, reveals, beams, columns, and the like | m2 | 105 |  |  |  |
| 3.244 | External Ceiling Finishes | - | 0 |  |  |  |
| 3.245 | Cement and sand (1:3) render 20mm thick mixed with an approved plasticiser on the following surfaces including preparation of surfaces to the approval of the Architect and as per Schedule of Finishes and Drawings. Rate shall include for hacking and labour for forming arises and fair edges, trowel smooth finish externally on: | - | 0 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 3.246 | Soffit of slabs and attached beams | m2 | 80 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 3.247 | DECORATION INTERNALLY | - | 0 |  |  |  |
| 3.248 | Prepare and apply one coat undercoat (clear emulsion binder) and two coats of approved emulsion based paint on the following rendered surfaces:- | - | 0 |  |  |  |
| 3.249 | Smooth rendered surfaces of : | - | 0 |  |  |  |
| 3.250 | walls, returns, reveals, beams, columns and the like | m² | 450 |  |  |  |
| 3.251 | Ceilings and the like | m² | 111 |  |  |  |
| 3.252 | Staircases | m² | 20 |  |  |  |
| 3.253 | Prepare and apply one coat undercoat (clear emulsion binder) and two coats of approved emulsion based acrylicanti fungus paint,colour to Architect`s approval on the following rendered surfaces:- | - | 0 |  |  |  |
| 3.254 | walls, returns, reveals, beams, columns and the like | m² | 70 |  |  |  |
| 3.255 | DECORATION EXTERNALLY | - | 0 |  |  |  |
| 3.256 | Prepare and apply one coat Undercoat (Clear emulsion binder) + 2 coats anti-fungus paint water repellant on the following rendered surfaces: | - | 0 |  |  |  |
| 3.257 | on sponge finished rendered surfaces of | - | 0 |  |  |  |
| 3.258 | walls, returns, reveals, beams, columns, and the like | m2 | 480 |  |  |  |
| 3.259 | Soffit of slabs and attached beams | m2 | 80 |  |  |  |
| 3.260 | SECTION 8 - SANITARY WARES AND FITTINGS | - | 0 |  |  |  |
| 3.261 | Supply and Fix the following sanitary appliances, complete with taps, stops, outlets and all supply and waste pipes, fittings and accessories as specifed and to approval of the Architect and specs and drawings G859/10 | - | 0 |  |  |  |
| 3.262 | Wash hand basin complete (Drop-in) | No. | 4 |  |  |  |
| 3.263 | European W.C complete with cistern and front seat cover | No. | 3 |  |  |  |
| 3.264 | Toilet Roll Holder | No. | 3 |  |  |  |
| 3.265 | Toilet Hand Spray | No. | 3 |  |  |  |
| 3.266 | Liquid soap dispenser | No. | 4 |  |  |  |
| 3.267 | Towel Rail | No. | 4 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 3.268 | Nappy Disposal Bin | No. | 1 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 3.269 | Pillar tap | No. | 4 |  |  |  |
| 3.270 | Disabled toilet complete with WC/Wash Hand Bssin /grab rail/soap dispenser/waste bin/toilet paper dispenser and the like. | Set | 1 |  |  |  |
| 3.271 | Supply Fix only the following accessories to the approval of the Architect as described in drawing G859/10 | - | 0 |  |  |  |
| 3.272 | Mirrors - 600x450x6mm thick bevelled edge mirror fixed with round-headed chrome plated screws on 8 mm thick cement fibre board backing | No. | 4 |  |  |  |
| 3.273 | Flexible hose - 12mm inclined bip tap with plastic flexible hose, trigger spray and wall hook | No. | 3 |  |  |  |
| 3.274 | Sanitary disposal | No. | 1 |  |  |  |
| 3.275 | Floor trap | No. | 4 |  |  |  |
| 3.276 | Hooks | No. | 4 |  |  |  |
| 3.277 | Low level tap including fittings | No. | 3 |  |  |  |
| 3.278 | SECTION 9 - SIGNAGE | - | 0 |  |  |  |
| 3.279 | Signage in acrylic sheet with black color icon fixed with inox screws to door at 1800 mm high all in accordance to Drwg No G859/13 and to the approval of the Architect. | - | 0 |  |  |  |
| 3.280 | Type S1 | No. | 1 |  |  |  |
| 3.281 | Type S2 | No. | 1 |  |  |  |
| 3.282 | Type S3 | No. | 1 |  |  |  |
| 3.283 | Type S4 | No. | 1 |  |  |  |
| 3.284 | Signage in acrylic sheet with lettering in black fixed with inox screws to door at 1800 mm high all in accordance to Drwg No G859/13 and to the approval of the Architect. | - | 0 |  |  |  |
| 3.285 | Type S5 | No. | 1 |  |  |  |
| 3.286 | Type S6 | No. | 1 |  |  |  |
| 3.287 | Type S7 | No. | 1 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 3.288 | Type S8 | No. | 1 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 3.289 | Signage in acrylic sheet(Green) with white lettering fixed with stainless steel cable wire to ceiling/beam all in accordance to Drwg No G859/13 and to the approval of the Architect and Engineer. | - | 0 |  |  |  |
| 3.290 | Type S9 | No. | 1 |  |  |  |
| 3.291 | Signage in stainless steel (brushed finish) light grey color,height of letters 250mm Font to be Times New Roman and with Hidden stainless steel fixations all in accordance to Drwg No G859/13 and to the approval of the Architect and Engineer. | - | 0 |  |  |  |
| 3.292 | Type S10 | No. | 1 |  |  |  |
| 3.293 | SECTION 10 - SUNDRIES | - | 0 |  |  |  |
| 3.294 | Stone Cladding | - | 0 |  |  |  |
| 3.295 | Stones joined with mortar cement and sand (1:3) and any interior pockets to be sealed with mass concrete.20mm thick waterproof rendering mortar (manufacturer`s specification for water proofing compound to be submitted for approval by Architect and Engineer on site).Holes should be drilled in R.C column and /or R.C beam.The holes should then be cleaned.The steel lugs should be anchored into the column and/or beam by chemically grouting to manufacturer`s specifications and to Engineer details and approval.Rate to include for concrete,necessary formwork,reinforcement,holes,finishes,pointing ,cutting,wastages,borders,labours and cleaning on completion and the like as per drawing G859/ST22 . | m² | 115 |  |  |  |
| 3.296 | Concrete worktop 1200mmx645mmx900mm high in Toilets finished with 20mm granite top and sides and wall tiles ,colour to Architect`s approval.Aluminium frame with stainless steel strip to be provided underneath worktop.Rate to include for concrete, necessary formwork, reinforcement, holes ,finishes,pointing of joint with coloured waterproof grout,cutting,wastages,borders,labours and cleaning on completion,furniture below worktop and the like ans as per Drwg No G859/11and to the approval of the Architect. | No. | 3 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 3.297 | Concrete worktop 1200mmx645mmx900mm high in Baby Changing Room finished with 20mm granite top and sides and wall tiles ,colour to Architect`s approval.Aluminium frame with stainless steel strip to be provided underneath worktop.Rate to include for concrete, necessary formwork, reinforcement, holes ,finishes,pointing of joint with coloured waterproof grout,cutting,wastages,borders,labours and cleaning on completion,furniture below worktop and the like ans as per Drwg No G859/11and to the approval of the Architect. | No. | 1 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 3.298 | Concrete counter in Information Office 1200mmx900mmx1000mm high comprising of high 50x50mm aluminium frame with 8mm laminated glazing and 300x300mm opening in glazing finished with 2 mm PVC edging and 20mm thick granite,colour to Architect`s approval to top and sides of counter.Rate to include for concrete, necessary formwork, reinforcement, holes ,finishes,pointing of joint,cutting,wastages,borders,labours and furniture below worktop and the like ans as per Drwg No G859/11and to the approval of the Architect. | No | 1 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 3.299 | Construct channel manhole overall size 6600mm x 600mm wideExcavate in any material including rock and build channel manholes with 125mm - 150mm thick reinforced concrete (Grade 30) bottom, 150mm thick reinforced concrete suspended cover slab rebated for precast cover 390 x300mm, 50mm thick blinding layer 1:4:8 mix, waterproof screed to bottom of manhole and waterproof rendering to internal walls, smooth trowelled finish, 20mm thick render to external surfaces and painted to Architect`s approval ,including all necessary formwork, reinforcement, holes, backfilling,finishes and the like all as per Drawing No. G859/ST07 and to the approval of the Engineer. | No. | 1 |  |  |  |
| 3.300 | Construct reinforced concrete platform for watertank on roof slab,2600x1600x150mm to Engineer`s details.Rate to include for concrete, necessary formwork, reinforcement, holes,finishes,waterproofing,fixation of watertank to platform and the like all as per Drawing No. G859/ST11 and to the approval of the Engineer. | No. | 1 |  |  |  |
| 3.301 | Construct concrete supports 250x250x250mm for water pipes on roof.Rate to include for concrete, necessary formwork, reinforcement, holes,finishes,waterproofing membrane and the like all as per Drawing and to the approval of the Engineer. | No. | 10 |  |  |  |
| 3.302 | Construct reinforced concrete canopy to openings to Engineer`s details. Rate to include for all necessary concrete works, formwork, reinforcement,rendering and painting,finishes and the like as per Architect`s and Engineer drawings and specifications. | - | 0 |  |  |  |
| 3.303 | Office-1850mm x500mm wide | No. | 1 |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 3.304 | Office-2000mm x 500mm wide | No. | 1 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 3.305 | Corridor-600 x 300mm wide | No. | 1 |  |  |  |
| 3.306 | ServerRoom-1500x300 mm wide | No. | 2 |  |  |  |
| 3.307 | Toilet-900mm x 300 mm wide | No. | 4 |  |  |  |
| 3.308 | Concrete window seat overall size 2425mm x 600 mm wide x 600 mm high in Main Hall finished with 20mm thick granite top and sides,colour to Architect`s approval.Rate to include for concrete,blockwall, necessary formwork, reinforcement, finishes,cutting,wastages,borders,labours and cleaning on completion as per Architect`s drawings and to the approval of the Architect and Engineer. | No. | 2 |  |  |  |
| 3.309 | Supply and fix varnished treated Balao Timber pergolas 100x 50 mm,wood colour to Architect`s approval,fixed to timber members 150x150mm including 150x100x10 mm thick galvanised MS plate and 270x140x10mm thick galv. MS plate with Galv M12 screw with point side penetration 100mm to Engineer details.All timber members to be finished with one coat wood primer and two coats varnish to Architect`s approval.All steel members to be treated with etch primer and painted with one coat of super galva primer,two coats of hard antifungus enamel paint to Architect`s approval and as per drawing G859/ST21. | m2 | 10 |  |  |  |
| 3.310 | SECTION 11 - SERVICES INSTALLATIONS | - | 0 |  |  |  |
| 3.311 | Work incidental to air conditioning, ventilation, plumbing, drainage, electrical, concealed fixings | - | 0 |  |  |  |
| 3.312 | Co-ordination with other engineering installations and marking and setting out the positions of all work | Item | 1 |  |  |  |
| 3.313 | Cutting or forming all holes, mortices, chases, corings, building in or cutting and pinning brackets or the like including all associated builder's work and making good finishings | Item | 1 |  |  |  |
| 3.314 | Building in or cutting and pinning brackets or the like and making good finishings | Item | 1 |  |  |  |
| 3.315 | Protective and decorative painting | Item | 1 |  |  |  |
|  | Total carried to summary sheet |  |  |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| ITEM NO | DESCRIPTION | Unit of Measure | QTY | Amount |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  |  | Rs | Cs |
| 4.0 | BILL NO 4- EXTERNAL WORKS | - | 0 |  |  |
| 4.1 | ADMEASUREMENT | - | 0 |  |  |
| 4.2 | EXTERNAL WORKS | - | 0 |  |  |
| 4.3 | SITE WORKS AND LEVELLING | - | 0 |  |  |
| 4.4 | Site Preparation | - | 0 |  |  |
| 4.5 | Clear sites of all bushes, scrub, vegetation, sugar cane roots, weeds, undergrowth, hedges and the like, including grubbing up roots and removing from site as directed | m2 | 1520 |  |  |
| 4.6 | Cut down trees, irrespective of girth, including grubbing up roots and removing from site and backfilling resulting pits with selected imported materials | Item | 1 |  |  |
| 4.7 | Excavate topsoil/fill material, average 500mm deep to be preserved, depositing in temporary spoil heaps as directed by the Engineer | m2 | 430 |  |  |
| 4.8 | Hardscaping and Landscaping | - | 0 |  |  |
| 4.9 | Grass planting including 150mm top soil arising from excavation or clean dry selected well graded imported topsoil to 150mm finishing layer with approved grass and well water and maintain until completion of works | m2 | 520 |  |  |
| 4.10 | Allow for maintaining, watering, weeding, cutting all grass areas for continuous healthy growth. Replace dead or decaying ones with fresh healthy stocks till end of Defects Liability Period all to the satisfaction of the Architect. | Item | 1 |  |  |
| 4.11 | Transplanting existing plants to new flower boxes | Item | 1 |  |  |
| 4.12 | Provide the following plants to new flower boxes to the approval of the Architect including topsoil from spoil heaps or from an approved source including haulage,transport,loading and unloading and well water and maintain the plants until completion of works all in accordance to Drwg G859/SW/03. | - | 0 |  |  |
| 4.13 | Palmiste Bouteille 1000mm high | No | 4 |  |  |
| 4.14 | Duranta Plant 400mm high | No | 32 |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 4.15 | Yucca Aloifolia Plant 1000mm high | No | 2 |  |  |
| --- | --- | --- | --- | --- | --- |
| 4.16 | Cannas Plant 400mm high | No | 44 |  |  |
| 4.17 | Queue De Chat Buisson Plant 400mm high | No | 19 |  |  |
| 4.18 | Snake Plant 400mm high | No | 20 |  |  |
| 4.19 | Aloe Vera Plant 400mm high | No | 2 |  |  |
| 4.20 | KERBS | - | 0 |  |  |
| 4.21 | Precast off shutter concrete kerb including all holes, chamfers, rebates, handling and transport, hoisting, fixing in position; jointing in cement mortar (1:3) , bedding and haunching in 200 mm thick concrete layer. Rate to include for all excavation. All as per structural engineer's drawing no G859/SW/ST03 | - | 0 |  |  |
| 4.22 | Kerb 150x300x1000mm long, Kerb K1 | m | 150 |  |  |
| 4.23 | RAMPS | - | 0 |  |  |
| 4.24 | Construct concrete ramp at Ground floor (Grade 1:12) as per Architect's and Engineer's drawings and specifications. Rate to include for all necessary excavation in all types of soil and rock, formwork, reinforcement, blinding, concrete works, filling and compaction under floor,fixing of 15mm expansion joints with approved sealant ,washed rocksand finish with average 900 mm concrete wall on both sides and sides ramp to be rendered and painted,colour to Architect`s approval and as per Architect and Engineer`s drawings. | - | 0 |  |  |
| 4.25 | Overall size 3500x1200mm | No | 1 |  |  |
| 4.26 | Overall size 3500x1400 mm | No | 1 |  |  |
| 4.27 | Overall size 11000x1500mm | No | 1 |  |  |
| 4.28 | RAMPS | - | 0 |  |  |
| 4.29 | Construct reinforced concrete ramp at Ground floor as per Architect's and Engineer's drawings and specifications. Rate to include for all necessary excavation in all types of soil and rock, formwork, reinforcement, blinding, concrete works, filling and compaction under floor,fixing of 15mm expansion joints with approved sealant ,finish with interlocking blocks ,colour to Architect`s approval all in accordance to Drwg No G859/SW/ST01&G859/SW/ST02 | - | 0 |  |  |
| 4.30 | Terrace-overall size 3000x2600mm | No | 1 |  |  |
| 4.31 | CONCRETE STEPS | - | 0 |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 4.32 | Construct reinforced concrete steps 4200mm long x 300 mm wide at Ground floorTerrace (RHS Elevation) as per Architect's and Engineer's drawings and specifications. Rate to include for all necessary excavation in all types of soil and rock, formwork, reinforcement, blinding, concrete works, filling and compaction under floor,fixing of 15mm expansion joints with approved sealant ,finished with 600x600x10mm thick (R10) heavy duty non-skid homogenous ceramic tiles (Marble effect) ,colour to Architect`s approval all in accordance to Drwg No G859/SW/ST01 | No | 2 |  |  |
| --- | --- | --- | --- | --- | --- |
| 4.33 | Construct reinforced concrete steps 3100mm long x 300 mm wide at Ground floor Terrace(Front Elevation) as per Architect's and Engineer's drawings and specifications. Rate to include for all necessary excavation in all types of soil and rock, formwork, reinforcement, blinding, concrete works, filling and compaction under floor,fixing of 15mm expansion joints with approved sealant ,finished with 600x600x10mm thick (R10) heavy duty non-skid homogenous ceramic tiles (Marble effect) ,colour to Architect`s approval all in accordance to Drwg No G859/SW/ST01 | No | 3 |  |  |
| 4.34 | SERVICE TRENCH & DRAINAGE INSTALLATION | - | 0 |  |  |
| 4.35 | Excavation in any material including rock or hard material, starting at formation level, for services,trimming bottom of excavations to regular falls backfilling with selected excavated material compacting as described and spreading surplus material on adjacent ground / remove surplus off site including earthwork support to sides of trenches, | - | 0 |  |  |
| 4.36 | 600mm wide x average 750mm deep | m | 125 |  |  |
| 4.37 | 800mm wide x average 1400mm deep (drainage) | m | 50 |  |  |
| 4.38 | 800mm wide x average 1400mm deep (cold water) | m | 70 |  |  |
| 4.39 | 300mm thick sifted soil filling laid to regular falls in trench in 100mm thick rocksand bedding and surround to PVC pipes and at least 100mm above crown of pipes and for the width of the trench, placing of warning tapes and complete backfilling of trench with 300mm thick sifted soil | - | 0 |  |  |
| 4.40 | 600mm wide x 750mm deep | m | 125 |  |  |
| 4.41 | Warning Tapes placed in trenches | m | 125 |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 4.42 | 300mm thick rocksand filling compacted in layers not exceeding 20mm and containing less than 12% fines, laid to regular falls in trench in 20mm thick compacted rocksand bedding 0/10 containing less than 10% fines and surround to PVC pipes and at least 100mm above crown of pipes and for the width of the trench and complete backfilling of trench with minimum 300mm thick crusher run 0.2 compacted in layes not exceeding 150mm | - | 0 |  |  |
| --- | --- | --- | --- | --- | --- |
| 4.43 | 600mm wide x 750mm deep | m | 125 |  |  |
| 4.44 | 600mm thick rocksand filling compacted in layers not exceeding 25mm and containing less than 12% fines, laid to regular falls in trench in 50mm thick compacted rocksand bedding 0/10 containing less than 10% fines and surround to PVC pipes and at least 100mm above crown of pipes and for the width of the trench and complete backfilling of trench with 700mm thick crusher run 0.2 compacted in layes not exceeding 150mm | - | 0 |  |  |
| 4.45 | 800mm wide x average 1400mm deep (drainage) | m | 50 |  |  |
| 4.46 | 800mm wide x average 1400mm deep (cold water) | m | 70 |  |  |
| 4.47 | CATCHPIT | - | 0 |  |  |
| 4.48 | Excavate in any material including rock and build catchpits of size 750 x550mm, depth varies 400-800mm ,with 100mm thick Mass Concrete bottom, 65mm thick concrete suspended cover slab rebated for precast cover 65mm thick reinforced with R6@150 mm both ways with lifting hole, 150mm thick blockwalls, waterproof concrete wall 1:2:4 mix, 50mm thick blinding layer Concrete Grade 15, 12mm thick waterproof screed to bottom and 12mm thick waterproof rendering to internal walls, smooth trowelled finish, including all necessary formwork, reinforcement, holes, backfilling and the like all as per Drawing No. G859/SW/ST03 | No | 3 |  |  |
| 4.49 | SOAKAWAYS | - | 0 |  |  |
| 4.50 | Excavate in any material including rock and build soakaways of size 3500 x1500x2500mm deep, remove surplus excavated materials off site, backfilling with hardcore of 200mm maximum size boulders and 31mm to 75mm maximum size agregate blinding levelled over hardcore to 400mm deep, laying of non-woven Geotextile Membrane of minimum weight per unit surface area of 200g/m including laps (measured nett) and laying of 100mm blockwork kerb with 50mm blinding layer at bottom of blocks and rendering to blocks, all as per Drawing No. G859/SW/ST03 | No. | 2 |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 4.51 | Excavate in any material including rock and build soakaways of size 1000 x1000x2500mm deep, remove surplus excavated materials off site, backfilling with hardcore of 200mm maximum size boulders and 31mm to 75mm maximum size agregate blinding levelled over hardcore to 400mm deep, laying of non-woven Geotextile Membrane of minimum weight per unit surface area of 200g/m including laps (measured nett) and laying of 100mm blockwork kerb with 50mm blinding layer at bottom of blocks and rendering to blocks, all as per Drawing No. G859/SW/ST03 | No. | 1 |  |  |
| --- | --- | --- | --- | --- | --- |
| 4.52 | MANHOLES | - | 0 |  |  |
| 4.53 | Excavate in any material including rock and build manholes 600x600mm,depth varies 600-1200mm with 150mm - 225mm thick reinforced concrete (Grade 30) bottom ,150mm thick reinforced concrete suspended slab rebated with cast iron cover diameter varies 600mm to 900 mm,150-200mm thick blockwalls, 75mm thick blinding layer 1:4:8 mix, Concrete benching 1:1:3 mix to secure half channels (Salt Glazed), waterproof screed to bottom of manhole and waterproof rendering to internal walls, smooth trowelled finish, including all necessary formwork, reinforcement, holes, backfilling and the like all as per Drawing No. G859/SW/ST03 | No. | 8 |  |  |
| 4.54 | Excavate in any material including rock and build manholes with 100mm thick reinforced concrete (Grade 30) bottom, hot dip galvanised steel covers of adequate thickness , reinforced concrete wall and 150-200mm thick blockwalls, 75mm thick blinding layer 1:4:8 mix, waterproof screed to bottom of manhole and waterproof rendering to internal walls, smooth trowelled finish, including all necessary formwork, reinforcement, holes, backfilling and the like all as directed by Engineer. | - | 0 |  |  |
| 4.55 | Type 1 (900x900mm) | No | 1 |  |  |
| 4.56 | Type 2 (1000x1000mm) | No | 2 |  |  |
| 4.57 | CONCRETE SEPTIC TANK | - | 0 |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 4.58 | Excavate for in any type of materials including rock and build reinforced concrete septic tank of size 4200 x 1500x 2000mm deep overall with 200mm thick reinforced concrete (Grade 30 N/mm²) bed, 200mm thick reinforced blockwall, 150mm thick reinforced concrete slabs, 75mm thick reinforced concrete baffle walls, 75 x 75mm angle fillet between junctions of walls and bed and junctions of walls, 75mm thick concrete (Grade 20 N/mm²) blinding, 25mm thick cement and sand (1:3) waterproof screed to falls, 25mm thick waterproof rendering to internal walls with a smooth trowelled finish including 3 Nr 510x660mm Heavy duty cast iron manhole cover and all necessary formwork, reinforcement, holes, backfilling, carting away surplus excavated materials and 110mm PVC inlet and outlet embedded in concrete and PVC Pipe of Diameter 80mm to be fixed vertically against 127x64 U channel all as per Drawing No. G859/SW/ST06 | No | 1 |  |  |
| --- | --- | --- | --- | --- | --- |
| 4.59 | Connection of new Septic tank to existing building prior to start of works of new building | Item | 1 |  |  |
| 4.60 | Connection of new Septic tank to new building after completion of new building | Item | 1 |  |  |
| 4.61 | ABSORPTION PIT | - | 0 |  |  |
| 4.62 | Excavate in any material including rock and build absorption pits of size 2100mm diameter, remove surplus excavated materials off site, backfilling with large stones to Engineer's specification, 31mm to 75mm maximun size agregate blinding levelled over hardcore to 400mm deep and 12mm to 20mm maximum size aggregate blinding levelled to 200mm deep and laying of 300x200mm Precast Concrete Kerb on blinding layer concrete grade 15/mm2 to perimeter of Absorption pit including mortar joints, cutting, curves, etc. all as per Drawing No. ED859/SW/ST06 | No | 1 |  |  |
| 4.63 | GULLY TRAP | - | 0 |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 4.64 | Excavate in any material including rock and build Gully Traps of size 650 x 650mm ,depth varies 600-900mm, with Mass Concrete bottom and concrete benching,125mm thick RC concrete suspended cover slab rebated with cast iron cover,100mm thick RC Walls, 75mm thick blinding layer Concrete mix 1:4:8 , 12mm thick waterproof screed to bottom and 12mm thick waterproof rendering to internal walls, smooth trowelled finish, including all necessary formwork, reinforcement, holes, backfilling and the like all as per Drawing No. G859/SW/ST03 | No | 2 |  |  |
| --- | --- | --- | --- | --- | --- |
| 4.65 | Pump room with water tank platform | - | 0 |  |  |
| 4.66 | Construct pump room of overall size 2000x1800 mm and concrete patform for water tank in reinforced concrete structure, blockwork, roof slab of 125 mm thick, galvanised metal door of size1200x2000mm, rendering and painting to internal and external walls and ceiling, screed to floor, waterproofing works to roof and pvc spout 50mm diameter. Rate to include for all necessary excavation in all types of soil and rock, formwork, reinforcement, blinding, concrete works, finishes and plumbing works all as per Drawing No G859/12 ,G859/SW/ST03 &G859/SW/ST04 | No | 1 |  |  |
| 4.67 | CEB CUBICLE | - | 0 |  |  |
| 4.68 | Construct CEB Cubicle of overall size 2950x960 mm in reinforced concrete structure, blockwork, roof slab of 125 mm thick, hot dipped galvanised metal doors, rendering and painting to internal and external walls and ceiling, screed to floor, waterproofing works to roof. Rate to include for all necessary excavation in all types of soil and rock, formwork, reinforcement, blinding, concrete works, finishes,flashing to be providedat top of cubicle along existing boundary wall all as per Drawing No G859/14 and G859/SW/ST07 | No | 1 |  |  |
| 4.69 | CONCRETE FLOWER BOXES (as per Drawing No ED667/SW/ST05) | - | 0 |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 4.70 | Construct reinforced concrete flower box of average size 20500 x 1000 in RC concrete structure including excavation and all necessary formwork, reinforcement, holes, backfilling and the like.Flower box to be rendered and painted on both sides and including topsoil filling to the approval of the Architect and all as per Architect and Engineer Drawings | No | 1 |  |  |
| --- | --- | --- | --- | --- | --- |
| 4.71 | Construct reinforced concrete flower box of average size 1400 x 900 in RC concrete structure including excavation and all necessary formwork, reinforcement, holes, backfilling and the like.Flower box to be rendered and painted on both sides and including topsoil filling to the approval of the Architect and all as per Architect and Engineer Drawings | No | 2 |  |  |
| 4.72 | Construct reinforced concrete flower box of average size 8000 x 2000 in RC concrete structure including excavation and all necessary formwork, reinforcement, holes, backfilling and the like .Flower box to be rendered and painted on both sides and including topsoil filling to the approval of the Architect and all as per Architect and Engineer Drawings | No | 1 |  |  |
| 4.73 | BOUNDARY WALL (as per DRG no. G859/12 and G859/SW/ST02) | - | 0 |  |  |
| 4.74 | Excavation in all types of soil including and construct retaining wall including backfilling, carting away excess material off site, compacting bottom of excavation, casting of blinding layer, strip footing and RC wall including formwork and reinforcement. supply and lay 12-20 aggregate fill, geotextile membrane and 75 mm diameter PVC pipe.Wall to be tyrolean finish on one layer plaster on both sides of wall and painted on both sides of wall,paint colour to Architect`s approval. | - | 0 |  |  |
| 4.75 | Boundary wall Type I | m | 36 |  |  |
| 4.76 | Retaining wall Type I | m | 10 |  |  |
| 4.77 | Retaining wall Type II | m | 17 |  |  |
| 4.78 | INTERLOCKING BLOCKS (as per DRG no. G859/SW/ST01 and G859/SW/ST03) | - | 0 |  |  |
| 4.79 | Excavate 550 mm deep in all types of soil | m3 | 97 |  |  |
| 4.80 | Cart away excavated material off site | m3 | 97 |  |  |
| 4.81 | Level grade to falls and compact as described reduced level to receive sub-base to interlocking blocks | m² | 175 |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 4.82 | Supply and lay 300mm thick approved hardcore filling composed of good hardstone ballast of size not greater than 100mm and compacted in layers not exceeding 225 mm | m² | 175 |  |  |
| --- | --- | --- | --- | --- | --- |
| 4.83 | Supply and lay 150 mm thick crusher run (0/20) compacted to 95% BS | m² | 175 |  |  |
| 4.84 | Supply and lay 25 mm thick rocksand compacted to specs | m² | 175 |  |  |
| 4.85 | Supply and lay 200x 100x60mm thick interlocking paving blocks laid in approved pattern laid to falls and crossfalls and to slopes including all holes ,mortices, chases, chamfers ,rebates ,handling ,transport ,labours,concrete Grade 30N/mm2 haunching, formwork,protection and cleaning on completion,all to the satisfaction of the Architect. | m² | 175 |  |  |
| 4.86 | GREEN PAVERS (as per DRG no. G859/SW/ST01 and G859/SW/ST03) | - | 0 |  |  |
| 4.87 | Excavate 550 mm deep in all types of soil | m3 | 180 |  |  |
| 4.88 | Cart away excavated material off site | m3 | 180 |  |  |
| 4.89 | Level grade to falls and compact as described reduced level to receive sub-base to green pavers | m² | 325 |  |  |
| 4.90 | Supply and lay 300mm thick approved hardcore filling composed of good hardstone ballast of size not greater than 150mm and compacted in layers not exceeding 225 mm | m² | 325 |  |  |
| 4.91 | Supply and lay 150 mm thick crusher run (0/20) compacted to 95% BS | m² | 325 |  |  |
| 4.92 | Supply and lay 25 mm thick rocksand compacted to specs | m² | 325 |  |  |
| 4.93 | Supply and lay concrete paving block-hollow 400x 600x 120 mm thick or equivalent including jointing,haunching,pointing on completion,including rocksand filling between blocks,levelling blocks,etc,as per Engineer`s details..Hollow to be filled with soil and planted with grass planting.Concrete paving block to be heavy duty for light traffic movement .Arrangement and colour pattern of blocks to be as per Architect`s approval | m² | 325 |  |  |
| 4.94 | COVERED DRAIN | - | 0 |  |  |
| 4.95 | Excavate in any material including rock and build covered drain of 450mm internal width, 200mm thick reinforced concrete (Grade 30) bottom, 640x450x190mm thick concrete cover slabs, 150mm thick reinforced concrete walls, 50mm thick blinding layer 1:4:8 mix, including all necessary formwork, reinforcement, holes, backfilling and the like all as Drawing No. G859/SW/ST03 | m | 11 |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 4.96 | GARBAGE BIN | - | 0 |  |  |
| --- | --- | --- | --- | --- | --- |
| 4.97 | Construct garbage bin of internal size 2650x1800 in reinforced concrete structure, blockwork, roof slab of 165 mm thick, hot dipped galvanised metal door, rendering and painting to internal and external walls and ceiling, screed to floor, waterproofing works to roof,aluminium flashing and 25 mm expansion joint between existing boundary wall and new garbage bin. Rate to include for all necessary excavation in all types of soil and rock, formwork, reinforcement, blinding, concrete works, finishes all as per Drawing No G859/12 and G859/SW/ST05 | No | 1 |  |  |
| 4.98 | FLAG POLE | - | 0 |  |  |
| 4.99 | 100 mm diameter steel pipe to BS 1387 (hot dipped galvanised) 6000mm high embedded in 700x700x1000mm high mass concrete with maximum 20 % 50-75 mm plums,200x200x6mm steel plate welded to pipe with metal halyard cleat welded to post,eye welded to tube and timber capping and painted with 1 coat of super galva primer,2 undercoat and one gloss finishing coat oil paint.Rate to include for all necessary excavation in all types of soil and rock,formwork,reinforcement,blinding,concrete works,finishes all as per Drawings. | No | 1 |  |  |
| 4.100 | LINE MARKING | - | 0 |  |  |
| 4.101 | Prepare and apply two coats of an approved road markings thermoplastic paint on tarred surfaces. | - | 0 |  |  |
| 4.102 | 150 mm wide lines,straight,continuous,colour to Architect`s approval | m | 35 |  |  |
|  | Total carried to summary sheet |  |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| ITEM NO | DESCRIPTION | Unit of Measure | QTY | Amount |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  |  | Rs | Cs |
| 5.0 | BILL NO 5- ELECTRICAL WORKS | - | 0 |  |  |
| 5.1 | ADMEASUREMENT | - | 0 |  |  |
| 5.2 | PART A: ELECTRICAL SYSTEM | - | 0 |  |  |
| 5.3 | Supply and install distribution panels/boards c/w switchgears and interconnecting cables as per schematics: | - | 0 |  |  |
| 5.4 | MDB (Type A) including manual changeover | No | 1 |  |  |
| 5.5 | SDB1 (Type B) | Lot | 1 |  |  |
| 5.6 | SDB2 (Type B) | Lot | 1 |  |  |
| 5.7 | DB-PH (Type B) | Lot | 1 |  |  |
| 5.8 | Supply and install following feeder cables: | - | 0 |  |  |
| 5.9 | From MDB to SDB1 (5C16mm2 + 5C10mm2) | Lot | 1 |  |  |
| 5.10 | From SDB1 to SDB2 (5C6.0mm2) | Lot | 1 |  |  |
| 5.11 | From SDB1 to DB-PH (3C4.0 mm2) | Lot | 1 |  |  |
| 5.12 | Supply, install, connect, wire, test and commission the following luminaires: | - | 0 |  |  |
| 5.13 | Luminaire Type A (LED Panel) | Nos | 30 |  |  |
| 5.14 | Luminaire Type B (Indoor Wall Lamp) | Nos | 6 |  |  |
| 5.15 | Luminaire Type C (Outdoor Wall Lamp) | Nos | 11 |  |  |
| 5.16 | Luminaire Type D (Waterproof 4ft) | Nos | 7 |  |  |
| 5.17 | Luminaire Type E1 (LED Landscape Spot Lights) | Nos | 4 |  |  |
| 5.18 | Luminaire Type E2 (LED Spot Lights) | Nos | 6 |  |  |
| 5.19 | Luminaire Type F (Ceiling Lamps) | Nos | 10 |  |  |
| 5.20 | Luminaire Type G (LED Floodlight) c/w IP65 enclosure 3x3 for connection | Nos | 2 |  |  |
| 5.21 | Luminaire Type I (Landscape Wall Lamp) | Nos | 4 |  |  |
| 5.22 | Luminaire Type J (Emergency Light) | Nos | 6 |  |  |
| 5.23 | Luminaire Type K (Pole Light) with pole minimum 6 metres high and reinforced concrete base to the approval of the Engineer. MCB2P10A on DIN Rail to be installed inside the pole with cover. | Nos | 10 |  |  |
| 5.24 | Supply, install, connect, wire, test and commission the following cables | - | 0 |  |  |
| 5.25 | Final circuit wiring for luminaires & switches | Lot | 1 |  |  |
| 5.26 | Armoured cables for pole lights | Lot | 1 |  |  |
| 5.27 | Final circuit wiring for sockets | Lot | 1 |  |  |
| 5.28 | Final circuit wiring for Double Pole Switches | Lot | 1 |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 5.29 | Final circuit wiring for rotary isolator Switches | Lot | 1 |  |  |
| --- | --- | --- | --- | --- | --- |
| 5.30 | Supply and install cableways: | - | 0 |  |  |
| 5.31 | Cable Trays | Lot | 1 |  |  |
| 5.32 | Underground PVC Sleeves for feeder cables | Lot | 1 |  |  |
| 5.33 | Underground PVC Sleeves for pole lights | Lot | 1 |  |  |
| 5.34 | Underground PVC Sleeves for pump house | Lot | 1 |  |  |
| 5.35 | PVC Conduit and Flexible conduit | Lot | 1 |  |  |
| 5.36 | Trunking | Lot | 1 |  |  |
| 5.37 | Supply, install, connect, wire, test and commission the following accessories: | - | 0 |  |  |
| 5.38 | Sockets 2G13A with indicator | Nos | 17 |  |  |
| 5.39 | Waterproof Sockets | Nos | 2 |  |  |
| 5.40 | Industrial socket 5-pin | No | 1 |  |  |
| 5.41 | Socket 1G13A for wall fans | Nos | 8 |  |  |
| 5.42 | Switches | Nos | 11 |  |  |
| 5.43 | Waterproof switches | Nos | 10 |  |  |
| 5.44 | DP Switches for ACs | Nos | 3 |  |  |
| 5.45 | DP Switches for Hand dryers | Nos | 4 |  |  |
| 5.46 | Dimmer 400W | No | 1 |  |  |
| 5.47 | Rotary isolator switch 40A for ceiling ACs similar to LEGRAND 7 353 02 | Nos | 4 |  |  |
| 5.48 | Hand Dryers | Nos | 4 |  |  |
| 5.49 | Extract Fans | Nos | 4 |  |  |
| 5.50 | Labeling, Testing and Commissioning including Test Certificate and as-made drawing in AutoCAD and Hard Copies. | Lot | 1 |  |  |
| 5.51 | PART B: FIRE DETECTION & ALARM SYSTEM | - | 0 |  |  |
| 5.52 | Fire Alarm Panel | - | 0 |  |  |
| 5.53 | Supply, install, test and commission a fire alarm panel c/w associated power supply, batteries and charger, etc all as per specifications. | Lot | 1 |  |  |
| 5.54 | Position of Fire Alarm Panel shown on drawings is indicative and may be relocated. |  |  |  |  |
| 5.55 | Wiring & Conduit | - | 0 |  |  |
| 5.56 | Supply and lay new cableway (trunking/conduit). | Lot | 1 |  |  |
| 5.57 | Allow for proprietary mounting bases for all items. |  |  |  |  |
| 5.58 | Supply and lay fire-retardant fire alarm cables | Lot | 1 |  |  |
| 5.59 | Fire Alarm Accessories | - | 0 |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 5.60 | Supply, fix, connect, test and commission the following fire alarm accessories: | - | 0 |  |  |
| --- | --- | --- | --- | --- | --- |
| 5.61 | Manual Call Points | Nos | 4 |  |  |
| 5.62 | Optical Smoke Detectors | Nos | 7 |  |  |
| 5.63 | Electric Sounders with strobe | Nos | 2 |  |  |
| 5.64 | Builders and reinstating works required, including but not limited to | Lot | 1 |  |  |
| 5.65 |  Fixing of all fire alarm accessories |  |  |  |  |
| 5.66 |  Fixing and Routing of all cable ways and wiring cables |  |  |  |  |
| 5.67 |  Carting Away |  |  |  |  |
| 5.68 | Any other builder’s work required to complete the work |  |  |  |  |
| 5.69 | Supply and deliver the following spares to the Client or his Representatives: | - | 0 |  |  |
| 5.70 | Manual call point | Nos | 1 |  |  |
| 5.71 | Optical smoke detector | Nos | 1 |  |  |
| 5.72 | Electric Sounder with strobe | Nos | 1 |  |  |
| 5.73 | Labelling, Testing and Commissioning including Test Certificate and as-made drawing in AutoCAD and Hard Copies. | Lot | 1 |  |  |
| 5.74 | PART C: AIR-CONDITIONING SYSTEM | - | 0 |  |  |
| 5.75 | Supply and install split AC unit of following capacity including refrigerant and drain pipes, fittings, insulation, trunking and accessories | - | 0 |  |  |
| 5.76 | 12,000 BTU/Hr wall type | Nos | 3 |  |  |
| 5.77 | 36,000 BTU/Hr ceiling type | Nos | 4 |  |  |
| 5.78 | Supply and install air curtains | Nos | 6 |  |  |
| 5.79 | Labeling, Testing and Commissioning including Test Certificate and as-made drawing in AutoCAD and Hard Copies. | Lot | 1 |  |  |
|  | Total carried to summary sheet |  |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| ITEM NO | DESCRIPTION | Unit of Measure | QTY | Amount |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  |  | Rs | Cs |
| 6 | BILL NO 6-MECHANICAL WORKS |  |  |  |  |
| 6.1 | ADMEASUREMENT |  |  |  |  |
| 6.2 | Cold water distribution system | - | 0 |  |  |
| 6.3 | Preamble | - | 0 |  |  |
| 6.4 | Cold water shall be supplied to sanitary wares and irrigation point on site. | - | 0 |  |  |
| 6.5 | All Buried pipes shall be HDPE PN16 except as specified elsewhere. | - | 0 |  |  |
| 6.6 | All surface pipes for cold water shall be UPVC PN16 except as specified elsewhere. | - | 0 |  |  |
| 6.7 | Cross linked polyethylene pipe (PEX) pipe shall generally be used for final connection to sanitary wares. | - | 0 |  |  |
| 6.8 | All transition fittings HDPE-UPVC to be fixed at 300 mm AFFL. | - | 0 |  |  |
| 6.9 | Contractor to allow for all fittings, pipe support, valves complete with all related accessories as detailed in the specification. | - | 0 |  |  |
| 6.10 | Sizes for pipe and valves shall be as shown in drawings. | - | 0 |  |  |
| 6.11 | All valves to comply with British Standard. | - | 0 |  |  |
| 6.12 | Pipelines and related accessories | - | 0 |  |  |
| 6.13 | Cold water pipelines | - | 0 |  |  |
| 6.14 | Buried pipe | - | 0 |  |  |
| 6.15 | Underground HDPE PN16 pipes with electrofusion weld joints, pipe fittings and accessories, buried within trenches with marker tape, unions, transition fittings, and any other required accessories. | - | 0 |  |  |
| 6.16 | Dia 50mm | m | 5 |  |  |
| 6.17 | Dia 25mm | m | 30 |  |  |
| 6.18 | Dia 20mm | m | 50 |  |  |
| 6.19 | Surface mounted pipe | - | 0 |  |  |
| 6.20 | Aboveground UPVC PN16 pipes with solvent welded joints, fittings support, unions, transition fittings and any other required accessories. | - | 0 |  |  |
| 6.21 | From roof water tank to sanitary wares | - | 0 |  |  |
| 6.22 | Dia 65mm | m | 3 |  |  |
| 6.23 | Dia 50mm | m | 3 |  |  |
| 6.24 | Dia 40 mm | m | 5 |  |  |
| 6.25 | Dia 32mm | m | 35 |  |  |
| 6.26 | Dia 20mm | m | 5 |  |  |
| 6.27 | Concealed pipe | - | 0 |  |  |
| 6.28 | Cross linked polyethylene pipe (PEX) Grade A pipe to EN ISO 15875 & DIN 16892, 6 Bar @ 95°C / 12.5 Bar @ 20°C with thermal memory effect and proprietary non-metallic fitting system, enclosed inside PVC sleeves c/w all related accessories for connection to uPVC | - | 0 |  |  |
| 6.29 | Dia 16 | m | 30 |  |  |
| 6.30 | Valves fixed on main pipes and manifold | - | 0 |  |  |
| 6.31 | Brass isolating/stop valves with stainless steel lever (ball type-lever operated). | - | 0 |  |  |
| 6.32 | Dia 65mm | nr | 1 |  |  |
| 6.33 | Dia 50mm | nr | 3 |  |  |
| 6.34 | Dia 40mm | nr | 1 |  |  |
| 6.35 | Dia 32mm | nr | 7 |  |  |
| 6.36 | Dia 25mm | nr | 1 |  |  |
| 6.37 | Dia 20mm | nr | 15 |  |  |
| 6.38 | Brass automatic air release valve complete with isolating valve fixed at the end of the pipework | - |  |  |  |
| 6.39 | DN 20 mm | nr | 2 |  |  |
| 6.40 | Chromium Plated Brass angle stop cock valve of European to the uPVC tubing c/w nut, roset for all sanitary wares. | - |  |  |  |
| 6.41 | DN 20 mm | nr | 14 |  |  |
| 6.42 | Bronze pipeline strainer with flanged joints, Y pattern body, minimum 250% screen free area of pipe bore |  |  |  |  |
| 6.43 | Dia 65mm | nr | 1 |  |  |
| 6.44 | Bip tap |  |  |  |  |
| 6.45 | Dia 20 | nr | 3 |  |  |
| 6.46 | Equipment | - | 0 |  |  |
| 6.47 | Pump as detailed in schedule. | - | 0 |  |  |
| 6.48 | Pump set consisting of two (2) pumps working on Duty/ assist/Standby (auto-changeover) mode and each rated at 1.0 l/s at 35m. Each pump to be equipped with Variable Speed Drive. Pump shall comply with the pump schedule. . | set | 1 |  |  |
| 6.49 | Fibre glass/polyethylene water storage tank | - | 0 |  |  |
| 6.50 | 9000 L capacity at ground floor | nr | 1 |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 6.51 | 2000 L capacity, Horizontal type fixed on roof | nr | 1 |  |  |
| --- | --- | --- | --- | --- | --- |
| 6.52 | Sleeves | - | 0 |  |  |
| 6.53 | Purpose made pipe sleeves of non-combustible material through walls, floors, ceilings | Lot | 1 |  |  |
| 6.54 | Dia 32 PVC sleeves | m | 5 |  |  |
| 6.55 | Manifold with three outlet to be provided inside pump room as shown in drawing. | nr | 1 |  |  |
| 6.56 | Sundries | - | 0 |  |  |
| 6.57 | Any other required equipment/accessories/valves in order to complete the installation as detailed in the specifications, schedule and shown on Mechanical Drawing series. | Lot | 1 |  |  |
| 6.58 | Labelling of equipment, pipework and Valve Colour Coding Identification in strict accordance to BS 1710 - Identification of Pipelines & Services and as specified. | Lot | 1 |  |  |
| 6.59 | Builders work related to the above-mentioned works. | Lot | 1 |  |  |
| 6.60 | Testing and commissioning | - | 0 |  |  |
| 6.61 | Testing and commissioning the whole of the foregoing system in accordance with the rules, regulations and requirements as described in the specifications. | Lot | 1 |  |  |
| 6.62 | ABOVE GROUND DRAINAGE | - | 0 |  |  |
| 6.63 | Preamble | - | 0 |  |  |
| 6.64 | The contractor is to determine the exact quantity of extra over pipes which are required to complete the works successfully and include them in the bid. | - | 0 |  |  |
| 6.65 | The sanitary pipework shall be a two-pipe system whereby WCs and urinals shall be connected to soil stacks whereas wash hand basins, showers, sinks and floor traps shall be connected to waste stacks. | - | 0 |  |  |
| 6.66 | Access points in the form of capped end fittings for rodding and cleaning purposes are to be provided in the reticulation network to facilitate clearance of blockages. | - | 0 |  |  |
| 6.67 | The price shall include connection to sanitary appliances. | - | 0 |  |  |
| 6.68 | Pipe shall comply with British/European standard. | - | 0 |  |  |
| 6.69 | Waste pipe from the existing building shall be diverted to the new septic tank. | - | 0 |  |  |
| 6.70 | Waste pipe from sanitary to Gully trap/manhole/grease trap/Inspection chamber | - | 0 |  |  |
| 6.71 | UPVC pipes straight, PN6, solvent welded all as shown in drawings. | - | 0 |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 6.72 | Pipe to be provided complete with pipe supports, fittings like bends, branches, tees, access plugs, couplings, saddles, reducers, bushes, adaptors, purpose-made odour prevention traps and related accessories, all as described and specified. | - | 0 |  |  |
| --- | --- | --- | --- | --- | --- |
| 6.73 | Dia 40mm | m | 10 |  |  |
| 6.74 | Dia 50mm | m | 20 |  |  |
| 6.75 | Dia 75mm | m | 10 |  |  |
| 6.76 | Dia 110mm | m | 10 |  |  |
| 6.77 | Accessories | - | 0 |  |  |
| 6.78 | PVC floor traps 100 x 100 mm with stainless steel cover brushed finish, shallow type to be concealed in slabs, DN 40 mm horizontal outlet. | nr | 5 |  |  |
| 6.79 | 110 mm vent cowl | nr | 1 |  |  |
| 6.80 | 75 mm vent cowl | nr | 1 |  |  |
| 6.81 | Pan adaptor, white PVC, 110 mm diameter with rubber seal sockets for WCs. | nr | 4 |  |  |
| 6.82 | PVC adjustable bottle trap with cleaning eye, 50 mm water seal depth, 32 mm trap internal diameter with screwed ends and enlargement fitting to connect to 50 mm dia pipe. | - | 0 |  |  |
| 6.83 | For WHB | nr | 4 |  |  |
| 6.84 | Re-routing of existing sewer/waste system | - | 0 |  |  |
| 6.85 | To dismantle any existing drainage pipe/fittings in the existing building where required for re-routing to the new septic tank. Contractor to allow for all required modification /fittings for connection to the new septic tank. | Lot | 1 |  |  |
| 6.86 | Sundries | - | 0 |  |  |
| 6.87 | PVC non-pressure sleeve cast in concrete for drainage pipes intumescent fire proof stopping compounds to BS 476-22, barriers, seals, mortar, mastic with fire-rated material for all pipe perforations and penetrations through walls/slabs/ceilings. | Lot | 1 |  |  |
| 6.88 | Pipework Colour Coding Identification in strict accordance to BS 1710 - Identification of Pipelines & Services and as specified. | Lot | 1 |  |  |
| 6.89 | Builders work related to the above-mentioned works. | Lot | 1 |  |  |
| 6.90 | Any other required equipment/accessories in order to complete the installation as detailed in the specifications and shown on drawings, schedules and schematics. | Lot | 1 |  |  |
| 6.91 | Testing and Commissioning | - | 0 |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 6.92 | Testing of the whole of the foregoing installation in accordance with the specifications and BS EN 12056-2. | Lot | 1 |  |  |
| --- | --- | --- | --- | --- | --- |
| 6.93 | BELOWGROUND WASTE PIPE | - | 0 |  |  |
| 6.94 | Preamble | - | 0 |  |  |
| 6.95 | The contractor shall be required to verify the cover level, invert levels of existing manholes, calculate the invert levels of the proposed manholes/inspection chambers for a fully functional drainage system and include them in shop drawings. The slope of pipes shall be as detail in specification. | - | 0 |  |  |
| 6.96 | The contractor shall be required to coordinate the drainage services with other services. | - | 0 |  |  |
| 6.97 | All pipes shall comply with British/European Standard. | - | 0 |  |  |
| 6.98 | Exact location of manholes, gully traps and grease traps shall be coordinated on site. | - | 0 |  |  |
| 6.99 | Concealed/buried waste pipe | - | 0 |  |  |
| 6.100 | UPVC pipes buried within trenches. | - | 0 |  |  |
| 6.101 | Pipes to be provided c/w SN8 rubber ring joints, couplings, sealing rings, adaptors, bends, tees, reducers, couplings, anchor blocks and related accessories, all as described and specified. | - | 0 |  |  |
| 6.102 | Dia 40mm | m | 4 |  |  |
| 6.103 | Dia 50mm | m | 4 |  |  |
| 6.104 | Dia 75mm | m | 6 |  |  |
| 6.105 | Dia 110mm | m | 5 |  |  |
| 6.106 | Dia 160mm | m | 25 |  |  |
| 6.107 | Re-routing of existing sewer network | - | 0 |  |  |
| 6.108 | Re-routing of existing sewer network to new manholes & septic as indicated on drawings. The contractor to allow for the cost for all accessories and any other items required for deviation of the existing sewer system. | Lot | 1 |  |  |
| 6.109 | Sundries | - | 0 |  |  |
| 6.110 | Any other required equipment/accessories in order to complete the installation as detailed in the specifications, schedule and shown on Mechanical Drawing series. | Lot | 1 |  |  |
| 6.111 | Testing and Commissioning | - | 0 |  |  |
| 6.112 | Testing of the whole of the foregoing installation in accordance with the specifications and BS EN 12056-2. | Lot | 1 |  |  |
| 6.113 | PORTABLE FIRE EXTINGUISHER | - | 0 |  |  |
| 6.114 | Preambles | - | 0 |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 6.115 | This section comprises of the supply and installation of portable CO2 and ABC powder fire extinguishers to be used by occupants of the building as first-aid fire-fighting means. | - | 0 |  |  |
| --- | --- | --- | --- | --- | --- |
| 6.116 | All portable extinguishers comply with British Standard and shall be wall mounted as indicated on fire fighting drawing series. | - | 0 |  |  |
| 6.117 | The location of these fire extinguishers shown in the drawings are for guidance only. Exact position to be finalized on site. | - | 0 |  |  |
| 6.118 | Equipment | - | 0 |  |  |
| 6.119 | 2Kg portable Carbon Dioxide (CO2) fire extinguisher as detailed in schedule. | nr | 2 |  |  |
| 6.120 | 4Kg portable ABC fire extinguisher as detailed in schedule. | nr | 2 |  |  |
| 6.121 | Photoluminescent rigid PVC fire signage | - | 0 |  |  |
| 6.122 | Type B signage for identification and location of portable carbon dioxide (CO2) fire extinguisher as detailed in schedule | nr | 2 |  |  |
| 6.123 | Type C signage for identification and location of portable ABC fire extinguisher as detailed in schedule | nr | 2 |  |  |
| 6.124 | Sundries, Testing and commissioning | - | 0 |  |  |
| 6.125 | Any other required equipment/accessories in order to complete the installation as detailed in the specifications and tender drawings | Lot | 1 |  |  |
| 6.126 | Testing and commissioning the whole of the foregoing installation in accordance with the rules and requirements, as described in the specifications. | Lot | 1 |  |  |
| 6.127 | Drawings and manual for the Mechanical Services as detail above. | - | 0 |  |  |
| 6.128 | Shop drawings shall be issued prior to start of any mechanical work. Shop drawing shall be in A1 size paper. All shop drawing shall be signed by a registered Mechanical Engineer. | - | 0 |  |  |
| 6.129 | Supply of 3 set of shop drawings in A1 size prior to installation of the whole Mechanical services. | Lot | 1 |  |  |
| 6.130 | Supply of 3 set of as made drawings in A1 size for the Mechanical services. | Lot | 1 |  |  |
| 6.131 | Supply of 3 set of Operation & Maintenance Manual for the Mechanical services. | Lot | 1 |  |  |
| 6.132 | Supply of 3 set of Operation & Maintenance Manual for the Mechanical services. | Lot | 1 |  |  |
|  | Total carried to summary sheet |  |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLAH

| ITEM NO | DESCRIPTION | Unit of Measure | QTY | Amount |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  |  | Rs | Cs |
| 7.0 | BILL NO 7 - DAY WORKS | - | 0 |  |  |
| 7.1 | The following are for labour, materials and plant available on site during the execution of the Contract Works and for works to be carried out on approved Daywork Basis. | - | 0 |  |  |
| 7.2 | PLANT | - | 0 |  |  |
| 7.3 | The rates inserted herein are to include all operational maintenance costs including fuel, oil, grease, spare parts, repairs, any extra costs of overtime and all superintendence, overheads and profit. The rates shall also include for all travelling time and costs for the plant operators, etc. to and from and about the site. Plant will only be paid for as Daywork when actually and necessarily engaged and working in Daywork operations. | - | 0 |  |  |
| 7.4 | Pneumatic compressors 160 CFM complete with drillers, breakers, chisels, plugs, feathers and the like | Hr | 5 |  |  |
| 7.5 | Excavator with hammer - JCB or similar | Hr | 5 |  |  |
| 7.6 | Concrete mixer (capacity 300 lts) | Hr | 5 |  |  |
| 7.7 | Bob Cat Loader / excavator | Hr | 5 |  |  |
| 7.8 | Tip truck of capacity 10T | Hr | 5 |  |  |
| 7.9 | Generator | Hr | 5 |  |  |
| 7.10 | Small tools and equipment | Hr | 5 |  |  |
| 7.11 | Poker vibrators complete | Hr | 4 |  |  |
| 7.12 | Grinder with diamond cutting disks | Hr | 5 |  |  |
| 7.13 | Electric breaker | Hr | 5 |  |  |
| 7.14 | Hand breaker - Hilthi or similar | Hr | 5 |  |  |
| 7.15 | LABOUR | - | 0 |  |  |
| 7.16 | The rates inserted herein are to include all costs of labour,including the use and maintenance of small tools and small plant such as scaffolding, trestles, wheelbarrows, picks,shovels, hard pumps, etc. any extra costs of overtime,insurances, accommodation, travelling times and expensesto and from sites, holiday pay, subsistence allowance, etc.together with all superintendence, overheads and profit.Where no rates are available for the works so prescribed,the wages customarily paid to the workmen concerned by other contractors executing similar works in Mauritius shall be applicable as on the date the daywork is carried out. | - | 0 |  |  |
| 7.17 | Unskilled labour | Hr | 5 |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| 7.18 | Skilled labour | Hr | 5 |  |  |
| --- | --- | --- | --- | --- | --- |
| 7.19 | Artisans- Masons, barbenders, carpenters, plumbers, electrician, all Grade I | Hr | 5 |  |  |
| 7.20 | Artisans- Masons, barbenders, carpenters, plumbers, electrician all Grade II | Hr | 5 |  |  |
| 7.21 | MATERIALS | - | 0 |  |  |
| 7.22 | The materials are all to be of qualities and descriptions stated in the specifications. The rates inserted herein are to include all loading, transport, unloading, storage, double handling, together with all overheads and profit. | - | 0 |  |  |
| 7.23 | Portland cement in 25kg bags | No. | 10 |  |  |
| 7.24 | Rocksand | Tonne | 2 |  |  |
| 7.25 | Washed rocksand (0-2) | Tonne | 2 |  |  |
| 7.26 | Aggregates 4mm - 20mm | Tonne | 2 |  |  |
| 7.27 | Mild steel reinforcement | Tonne | 2 |  |  |
| 7.28 | High yield steel reinforcement | Tonne | 2 |  |  |
| 7.29 | Hollow concrete blocks 500 p.s.i | - | 0 |  |  |
| 7.30 | 200 mm | m² | 20 |  |  |
| 7.31 | 150 mm | m² | 20 |  |  |
| 7.32 | 100 mm | m² | 20 |  |  |
| 7.33 | Formwork Class 1 (Fair face) | m² | 20 |  |  |
| 7.34 | Formwork Class 2 (Sawn formwork) | m² | 20 |  |  |
| 7.35 | One coat emulsion binder, 1 coat emulsion paint and 2 coats paint | m² | 50 |  |  |
| 7.36 | Enamel gloss oil paint (One primer, two undercoats and 1 enamel gloss finishing on metal surfaces | m² | 40 |  |  |
| 7.37 | Varnish (One coat sealer and three coats timber varnish) | m² | 40 |  |  |
|  | Total carried to summary sheet |  |  |  |  |

NEW COMMUNITY WELLNESS CENTRE AT GOKOOLA

| ITEM NO | DESCRIPTION | Unit of Measure | QTY | Amount |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  |  | Rs | Cs |
| 8.0 | BILL NO. 8 CONTINGENCY SUM | - | 0 |  |  |
| 8.1 | Allow the contingency sum of Rupees One Million and Five Hundred Thousand . (Rs 1,500,000) to be used at the discretion of the employer & deducted in whole or part, if not required. | Sum | 1 |  |  |
|  | Total carried to summary sheet |  |  |  |  |

SUMMARY

| S/N | Brought forward from | Amount (Excluding VAT) |
| --- | --- | --- |
| 1 | BILL NO. 1 PRELIMINARIES AND GENERAL COSTS |  |
| 2 | BILL NO. 2 DEMOLITION WORKS |  |
| 3 | BILL NO. 3 COMMUNITY WELLNESS CENTRE |  |
| 4 | BILL NO. 4 EXTERNAL WORKS |  |
| 5 | BILL NO. 5 ELECTRICAL WORKS |  |
| 6 | BILL NO. 6 MECHANICAL WORKS |  |
| 7 | BILL NO. 7 DAYWORKS |  |
| 8 | CONTINGENCY SUM |  |
| 9 | TOTAL CARRIED TO BID SUBMISSION FORM |  |

4. Form of Key Financial Information extracted from Audited Accounts/ Financial Statements

| Financial data in the currency reported in the Audited Accounts/Financial Statements | Historical Information |  |  | Remarks By BEC |
| --- | --- | --- | --- | --- |
|  | Previous years | Last year | Current year |  |
| Statement of Financial Position (Information from Balance Sheet) |  |  |  |  |
| A. Current Assets |  |  |  |  |
| B. Current Liabilities |  |  |  |  |
| Working capital ratio or current ratio( A/B) |  |  |  |  |
| Quick ratio or Acid Test ratio (Current Asset net of stock / B) |  |  |  |  |
| C. Total Assets |  |  |  |  |
| D. Total Liabilities |  |  |  |  |
| Net Worth( C-D) |  |  |  |  |
| Cash in hand and at Bank |  |  |  |  |
| Bank Overdrafts |  |  |  |  |
| Other Liquid Assets |  |  |  |  |
| Information from Income statement |  |  |  |  |
| Key Profitability Indicators in the currency reported in the Audited Accounts/Financial Statements | Previous years | Last year | Current year |  |
| Turnover |  |  |  |  |
| Profit /(Loss )Before Tax |  |  |  |  |
| Taxation |  |  |  |  |
| Net Profit /(Loss) After Tax |  |  |  |  |
| (Net profit After tax )x 100 (Turnover) |  |  |  |  |
| Certified by Bidder that information are true extract from Audited Accounts/Financial Statements Name: Signature: Capacity: Date: |  |  |  |  |

Section III: Statement of Requirements

SCOPE OF WORKS

The project consists of the construction of a New Community Wellness Centre and other related works at Gokoola as described hereunder:

1.  Demolition works of existing part of boundary wall, kerbs, low wall and fencing,

steps, absorption pit, flower boxes as per drawings.

2.New Building

The New Community Wellness Centre consists of the following:

Ground floor (Main Building):

- Entrance

- Front ramp

- Lobby

- Main hall

- Terrace

- Two ramps for disabled & emergency exit

- Corridor

- Toilet for staff (Female)

- Toilet for staff (Male)

- Female and male toilets

- One toilet for disabled

- Server Room

- Information Office

- Court yard

The construction of a new single storey Community Wellness Centre in reinforced    concrete structure, finished with the following works; - internal and external rendering/painting, ceramic floor tiles and wall tiles, waterproofing works, pergola and false ceiling, plumbing and drainage installations works, electrical works, rain water pipes, aluminium doors and windows, burglar proofing, timber openings, interior plants and site works and other miscellaneous works described in the bid documents.

3.External services installation works comprising rainwater installation works such as catch pits, gully traps, soak aways, waste water installation works such as manholes, channel manholes, septic tank, absorption pit, water supply works, electrical main supply and electric manholes. Works shall include reinstatement of damaged underground pipes and cables and other services that may be met with.

4. Provision of all piping including water supply, water tank, waste, floor traps, connection to   covered drain, soakaways, etc. as per Mechanical Engineer.

5.Hoarding shall be provided to secure contractor’s workspace and the site. Hoarding shall be to the satisfaction of the Project Architect and Project Structural Engineer.

6.Site works such as disabled parking, visitors parking, interlocking block, grass planting, CEB cubicle, pump room, garbage bins, boundary wall, green pavers, flower boxes, concrete platform for water tank, covered drains and landscaping and plants.

7.Works include reinstatement of damaged structures and finishes incidental to

construction works.

8.Other works as more fully described in the drawings, specifications and other

parts of the Bid document.

General Notes

All necessary precautions such as security nets among others have to be installed all along the scaffolding for security of the occupiers. It is to be noted that the building will be operational during the construction works.

Contractor to take note

(i)	Any damage of existing services and property during execution of works shall be reinstated or replaced to the satisfaction of the Architect/ Engineer at no additional cost.

(ii)	To ensure cleanliness throughout the circulation and construction areas.

(iii)	Contractor to ensure that no disturbances are caused to the premises during execution of the movement of materials and works.

(iv)	Contractor to make his own arrangement for power supply and provision of water on site.

Special conditions:

(i)	Contractor is informed that the works shall be executed while the building will be operational. Therefore, the contractor is to ensure that the building must be fully functional and consequently certain works will need to be carried out outside office hours.

(ii) 	Particular precautions shall be taken with respect to the safety and security of the occupants within the entire building premises.

(iii)	Contractor shall make provision to execute noisy works outside normal office hours.

(iv)	Loading and unloading of building materials, carting away of debris, movement of vehicles to be effected before and after office hours, during weekends and public holidays.

(v)	The Contractor may have to carry out works during weekends, public holidays and during odd hours and the same should be allowed in the bid price.

SPECIFICATIONS

The Government of Mauritius Standard Specifications issued by the Ministry of National Infrastructure & Community Development shall form part of the contract documents (Refer Appendix I ).

All materials used in this project should be to the approval of the Architect and Engineer.

With reference to the “Standard Specifications”, kindly note that:-

An Approved Testing Authority is further defined as:-

- Materials Testing Laboratory

- Mauritius Standard Bureau

- The Laboratory of the University of Mauritius

Additional Specifications

GRASS PLANTING

(a)	Clean the whole site, remove bushes, shrubs, plants vegetarian and boulders.  Uproot all existing trees trunks and roots, cart away all unwanted materials.

(b)	Level the ground by cutting and filling, bringing the levels as shown on the whole area with heavy roller and make good all depressing by additional imported good soil wherever necessary.

(c)	Supply and spread a layer of 300 mm vegetable soil compacted thickness.

(d)	Plant grass ‘Chiendent &Bourique’ using fertilizer and maintain watering till there is sign of healthy spread over.

ANTI-TERMITE TREATMENT

The anti-termite treatment must create a complete chemical barrier in the sub-structure of the buildings.  A 10-year guarantee certificate must be provided to the approval and satisfaction of the Employer.

PAINTS

External coating paints shall be waterproof and be guaranteed against discoloration, bacterial growth, cracking, chipping and peeling off from the masonry surfaces for a period of not less than Five (5) years.

All paints, stains and varnishes applied shall be eco-friendly with zero VOCs (Volatile Organic Compounds) or low VOCs (less than 5%).

ALUMINIUM WINDOWS AND DOORS

1.0	GENERAL

1.1	Submission

- Submit shop drawings

- Show detailed window assembly, including: large scale details of members and materials, of brackets and anchorage devices and of connection and jointing details fully dimensioned layouts for positioning of brackets and anchorage devices structures, dimensions gauges, thickness, glazing details, description of materials including catalogue members, products and manufacturer’s names, aluminium alloy and temper designations, finish specifications and all other pertinent data.

- All the above submissions shall be duly signed by a registered Professional Engineer

1.2	DELIVERY AND STORAGE

1.	Adequately protect aluminium and aluminium finishes to prevent damages thereto during fabrication, storage shipping, handling and installation.

2.	Deliver, handle and store units by methods approved by manufacturer.  Protect from damage and staining.

3.	Protect stills and stools after installation with boards heavy paper or other suitable protection, secured in place, to prevent staining or scratching.  Do not remove protection before final cleaning.

1.3	WARRANTY

1.	The contractor shall submit a warranty of five years in writing from the manufacturer.

2.	In addition to the above, insulating glass units shall carry manufacturer’s standard warranty of minimum five years for defective materials.

- The warranty shall include resistance to cyclonic winds of not less than 280 km/hr and water tightness.

- The contractor shall submit a certificate from a registered professional engineer certifying that Aluminium openings fixed in place shall withstand wind speed of not less than 280 km/hr.  This certificate shall in no way waive or diminish the contractor’s liability towards the employer.

- The contractor shall fill and submit the “Certificate for Aluminium openings” as annexed form.

- PRODUCTS

  - MATERIALS

      - Powder coated (colour to Architect approval) to be indicated to all aluminium openings, (except where specified).

      - Notes for Aluminium Openings to be simplified as follows:

- Aluminium Openings shall be of aluminium alloy 6060 A.G.S.

- Aluminium extrusions – powder coated .

- Openings to be water tight, air tight and resistant to wind load and to withstand cyclonic winds as per current wind gusts pressure over 280km/hr substantiated with calculations and certificates as required and to the approval of the Architect/Engineer.

- Handles, locks, hinges & knobs to be of heavy duty type.

- Bolts, screws and fasteners: 316 Stainless Steel.(Certificate to be produce for stainless steel grade).

- Glazing (Glass: Laminated glass of minimum thickness 6 mm).

- Gasket (E.P.O.M) as per manufacturers’ specifications.

- Corner cleat and any other reinforcement to be used must be of same aluminium mat.

3.	Glazing Tape: Vulcanised butyl tape with continuous neoprene spacer, colour as selected by Architect

4.	Setting Block: Neoprene 10 mm long, 80A durometer.

5.	Steel: Brake formed, galvanized sheet steel.

Notes: All Aluminium Openings including fittings to be of BS or EN or equivalents (to Architect’s approval). For equivalents, Contractor to submit Compliance Certificate from an independent and approved body.

- EXECUTION

DESIGN

1.	Allow full expansion and contraction of window framing members without causing stress within the window assembly as result of such expansion and contraction.

2.	Tolerate structural deflection and distortion structure, under design criteria conditions, without imposing load on window assembly

FABRICATION

- Make profiles of framing members as shown on drawings.

- Entire assembly shall be weather- tight throughout.

- Fabricate complete units in shop to provide minimum tolerance and hairline joints throughout.

- Assemble members by stainless steel screws.  All connections shall be internally sealed in factory with approved sealing compound.  Exposed frame sealants are not acceptable.

- Aluminium extrusions shall be designed to provide sufficient section modules to safety resist imposed loads but minimum thickness of any part of the load bearing extrusion shall be 3 mm.  Glazing stops may be 6 mm.  Be prepared to submit design date as requested by Architect.

- Conceal interconnecting members and fasteners in completed assembly.

- Do not place manufacturer’s name plates, labels or any other finished means of identification on exposed of finished parts.

- Provide weep holes on tubular members to drain and condensation.

- Glass stops shall provide edge margins recommended by glass manufacturer.

- Paint all metal surface in contact with concrete or masonry, plastic, mortar or dissimilar metals with protective lacquer or bituminous coating.

- Mitre and full strength vulcanize joints in weather- stripping.

- INSTALLATION

1.	Provide all fastenings or anchors required to be built in under work of other Sections.

2.	Use only concealed fastenings.

3.	Securely install components so that they line up square in true, straight flat and/or flush planes, plumb and level free from distortion.

4.	Make joints neat and fine as practicable.  Allow for full expansion and contraction and take into consideration climatic conditions prevailing at time of installation.

5.	Fasten galvanized steel supports and clips with galvanized bolts and fasten aluminium members with stainless steel screws and bolts.

- Ensure that corner joints of frames are weather-tight.

- Clean aluminium and glass surfaces that are to receive glazing materials with an oil removing solvent and wipe dry.

- Glaze windows with factory glazed wrap around vinyl glazing channels.

- Place setting blocks at quarter points for each type of glass.

- Comply with tape manufacturer’s recommendations regarding use of spacers for certain glass sizes.

- Install glass with clean cut edges, leaving spaces to expansion and contraction between edge of glass and inside of frame as recommended by glass manufacturer.

- Finish tape and glazing wedge with straight unwaving sight lines.

- Conform to sealant manufacturer’s written recommendations for cleaning, priming, backing and joint design to suit type and location of joint and temperature conditions at time of application.

- Mask adjacent surface likely to become marred with sealant or primer, using non-thermosetting easily removed masking.

- Apply sealant using pressure operated gun fitted with suitable nozzles approved by the sealant manufacturers.  Apply in accordance with manufacturer’s directions and recommendations.

- Apply sealant in such a manner as to assure good adhesion to sides of joints and to completely fill voids in joints.  Form surfaces of sealant smooth, concave, free from ridges, wrinkles, sags, air pockets and imbedded impurities.

- Remove masking tape, soils and sealant which may have been deposited on surfaces near joints.

- Seal all window frames to adjacent materials both sides.

- CLEANING

- When directed, inspect work and remove protective wrappings, coatings and devices and clean glass and aluminium surfaces.  Use methods which will not scratch or damage glass, paint or coatings.

CERTIFICATE FOR ALUMINIUM OPENINGS

In accordance with the requirements of (Clauses 1.1 and 1.3) of the Specifications of the contract for the Supply and fixing of Aluminium Openings for the project (Name of Project)………………………………………………………………………………………………………………………………………………… I, the undersigned Registered Professional Engineer, hereby certify that the aluminium openings which have been fixed at (Location) ………………………………………………………………………………………………….

have been designed and fixed to resist cyclonic winds of 280 Km/hr.

Name of Engineer:………………………………………………………………………………………

Registration Number with the Council

of Professional Engineers:…………………………………………………………………………

Signature:…………………………………………………………………………………

The following part is to be signed by the Contractor.

In the event of a failure of these openings due to cyclonic winds of 280 km/hr or less, (Name of Contractor) ………………………………………………………………………………………………………………………..undertakes to replace these openings and make good all damages resulting from the failure of these openings.

Name:…………………………………………………………………………………….

In the capacity of:……………………………………………………………………

Signed:……………………………………………………………………………………

Duly authorized to

Sign the certificate for and

on behalf of:…………………………………………………………………………..

Date:……………………………………………………………………………………….

Seal of Company:……………………………………………………………………

SPECIFICATIONS OF THE WATERPROOFING SYSTEM

The Subcontractor for waterproofing works must be specialist waterproofing contractors registered with the CIDB.

1.0	The Waterproofing System

The waterproofing system, unless otherwise specified, shall meet the following performance specifications:

either (a) a SBS elastomeric bitumen system in double layers, torched bonded and of total minimum thickness of 4.2 mm with a granular finish, as described below:

- The first layer should be a SBS(Styrene – Butadiene – Styrene) elastomeric bitumen system reinforced with non-woven glass fibre Md(50 gm2) torched applied with a minimum thickness of 1.7 mm.

- The second layer should be a SBS (Styrene – Butadiene – Styrene) elastomeric bitumen system reinforced with non woven glass fibre matt having a minimum thickness of 2.5 mm. This layer should have a highly reflective white slate flakes finish to help the cooling down of the  surface temperature of the roofing system by reflection and applied by torch.

or 	 (b)  a PVC system of minimum thickness of 1.2mm, mechanically fastened and  welded at joints.

OR

Any other alternative system, provided it is duly supported with all technical specifications and backup information and literature to allow a proper assessment of the treatment proposed.

- Performance Specifications of the Waterproofing System

2.1 	The system shall be capable of accepting minor structural movements without damage.

2.2 	The system shall be such as to prevent the growth of plants on it.  It shall be root resistant.

2.3	The system shall not be adversely affected by waterponding and shall be rot resistant.

2.4	The system shall be fire resistant up to 3 hours.

2.5	The system shall resist cyclonic winds of 280 Km per hour.   This shall be confirmed in writing by the Manufacturer, Socotec, Bureau Veritas or a Registered Professional Engineer.

2.6	The system shall be, unless specified otherwise, resistant to foot traffic and light concentrated loads associated with installation and maintenance operations.

2.7	The system shall comply to European, American or South African Standards.

2.8	The system and its installations shall conform strictly to Manufacturer’s specifications.

2.9	The system to be UV stable.

3.0	Preparation of surface to receive the Waterproofing treatment

3.1	The Waterproofing Contractor shall ensure that the slope of the substrate is adequate to prevent waterproofing and is according to Manufacturer’s Specifications.

3.2	The surface of the substrate shall be reasonably smooth and free from holes and projections which might puncture or otherwise damage the waterproofing system to be applied.

3.3	The surface of the substrate shall also be dry and shall be thoroughly cleaned of dust and loose materials prior to the laying of the waterproofing system.

3.4	After being satisfied with the above conditions, the waterproofing Contractor shall then issue a certificate stating that the substrate, which is to receive the new waterproofing system, is according to Manufacturer’s Specifications.

4.0	Application of the Waterproofing System

The waterproofing system shall be applied by experienced and skilled labour.

The waterproofing Contractor shall be required to provide proof of the experience and skill of its proposed labour on the works.

5.0	Inspection of Waterproofing System

5.1	The waterproofing treatment shall be carried out to the satisfaction of the Architect.

5.2	The Contractor shall ensure that the waterproofing system is free from wrinkles, buckles, blisters (trapped air) and other damage.  Any damage or defects to the waterproofing system shall be corrected at the Contractor’s cost, and to the Architect’s approval.

5.3	The contractor shall carry out a water test on the finished work, and seek the Architect’s approval for the same. The test shall consist in filling the whole treated area with water (after plugging the rainwater pipes outlets) and retaining the water on the treated surface for 24 hours, or as directed by the Architect. Any leak/defect found shall be repaired at the Contractor’s cost and another water test carried out to confirm the same, the whole to the Architect’s satisfaction.

5.4	The contractor shall clean adjacent surfaces of spillage and spatterings of any adhesive materials used in the works.

6.0	Water Test

6.1 	The contractor shall allow in his rates for a water test to be carried out after laying the screed to fall, to confirm the absence of any water-ponding. The Test shall be verified and approved by the Architect.

7.0	Guarantee Certificate

7.1	On satisfactory completion of the waterproofing works, the Contractor shall submit a certificate of guarantee against leakage, defective materials and defective installation of the completed waterproofing system.  Any such defects or leakage occurring during the guarantee period shall be promptly and completely corrected, including all affected work, at no additional cost to the Employer.

7.2	The said guarantee shall be in effect for a period of ten (10) years from the date of the practical completion certificate.  The guarantee shall be signed by the Contractor and countersigned by the Manufacturer’s representative and shall be submitted to the Employer.

TIMBER  SPECIFICATIONS

JOINERY WORK GENERALLY

All joiner’s work generally shall be cut and framed together on the commencement of the works, but shall not to be wedged up or glued until the building is ready for fixing same.

All work shall to be properly, tennoned, shouldered, wedged, pinned, bradded, etc. as directed and to the satisfaction of the Interior Designer and all properly glued up with best quality approved glue.  Oval or round brads or nails shall be used for fixing on face work, heads properly mails punched in and the holes filled with putty or as otherwise described.

WARRANTY

The contractor shall submit a guarantee of five (5) years against warping, cracks, shrinkage and distortion.

FINISH TO WOODWORK

All exposed faces of woodwork shall be wrot, which shall mean bringing up the surface after planning with sand paper to a smooth satin like finish.

DOOR FRAMES AND LININGS

Door frames and linings shall be constructed to the sizes and details shown on the drawings.  Joints between style and head shall be mitred.

Fixing irons shall consist of 300 mm long g.m.s hoop not less than 3 mm thick bent up at 75 mm at one end and twice screwed to the frame and the other end built into the walls, and cast into lintols to the depth of 225 mm deep, the straps shall be cut off to the full depth of the lintol.

10 mm diameter galvanized metal dowels shall be fixed to each end of the frames and let into the floor concrete to a depth of at least 50 mm.

Door linings shall be screwed to wooded fixing dovetail shaped and let into the walls and lintol with the same number of fixing irons to frames.

DOORS

Doors shall be provided and fixed to the sizes and details shown on the drawings.  Doors shall be free from all blemishes and shall be rubbed down to a satin like finish.  Framed, ledged and braced doors shall be made to the sizes shown on the drawings and the nailing in construction shall be driven from the face side, the heads of nails shall be punched d the holes filled with putty.

Butts and hinges shall be to the sizes and type specified and be fixed with the full number of screws and on no account shall nails be used.

PLYWOOD

Plywood shall be to the specified thickness and shall comply with BS 1455, plywood shall be Grade 1 where varnished and Grade 2 where painted.  Concealed side of plywood can be Grade 3.

BLOCKBOARD

Blockboard shall be to thickness shown on drawings and shall conform to BS 3444 and 3583.

GLUES

All glues to be used for joinery works shall be the best of their respective kind and shall conform to BS 745,1444,1203 and 1204.

SCREWS

Screws to be used for the joinery works shall be brass and shall conform in every respect to BS 1210.

NAILS

Nails shall be galvanized mild steel wire nails – all on accordance with BS 1202.

MOISTURE CONTENT OF TIMBER

The Contractor is to ensure that the moisture content of the various items if joinery delivered to the site should be at least 12%.

SHRINKAGE

The arrangement, jointing and fixing of all joinery works shall be such that shrinkage in any part and in any direction shall not impair the strength and appearance of the finished work and shall not cause damage to contiguous materials or structure.

TOLERANCE

Reasonable tolerance shall be provided at all connections between joinery works and the building carcass, whether of masonry or frame construction, so that any irregularities, settlements or other movements shall be adequately compensated.

FABRICATION

The joiner shall perform all necessary mortising, tennoning, grooving, matching, tonguing, housing, rebating and all other works necessary for correct jointing.  He shall also provide all metal plates, screws, nails and other fixings that may be ordered by the Interior Designer or that may be necessary for the proper execution of the joinery works specified.  The joiner shall also carry out all works necessary for the proper construction of all framings, linings, etc. and for their support and fixing in the building.

JOINTS

The joinery shall be constructed exactly as shown on the Interior Designer’s details.  Where joints are not specifically indicated they shall be the recognized forms of joints for each position.

The joints shall be made so as to comply with BS 1186, Part 2: 1971.

Loose joints are to be used where provision must be made for shrinkage or other movement acting other than in the direction of the stresses of fixing or loading.

Glued joints are to be used where provision need not be made for shrinkage or other movements in the connections, and where sealed joints are required.

All glued joints shall be cross-tongued or otherwise reinforced.

All nails, sprigs, etc., are to be punched and puttied.

Where glued joints are to be carried out surfaces in contact are to have a good swan of planed finish.  All cutting edges of tools are to be sharp to avoid “burnishing”.  The surface of plywood to be glued should be lightly dressed with sand or glass paper.  The sand or glass paper must not be allowed to clog and cause “burnishing”.

Members in constriction to be joined by gluing are to be of similar conversion.  All surfaces to be glued are kept clean, free from dirt, sawdust, oil and any other contamination.

Adequate pressure should be applied to glued joints to ensure intimate contact is maintained whilst the glue is setting.

Mixing application and setting conditions should be in accordance with the glue maker’s instruction.

“Adhesives” for joints in non-loadbearing internal work and for joints in work where the moisture content is always less that 16 per cent can be casein or organic glues.

For work under damp conditions (moisture content normally 20 per cent or more or conditions liable to fungal attack): resin type adhesive are to be use

SCRIBING

All skirtings, architraves, plates and other joinery works shall be accurately scribed to fit the contour of any irregular surface against which they may be required to form a close butt connection.

FLUSH DOORS

Flush doors shall be semi-solid cored and shall be lined on both sides with 4 mm Grade 2 plywood for painting or 4 mm Grade 1 teak plywood where shown.

The doors shall be lipped with 10 mm thick hardwood strips on (4) for sides and shall be fitted and hung to frames as detailed on drawings and specified previously.

Doors shall otherwise conform to BS 459.

PROCEDURE

MEASUREMENTS FOR JOINERY

The Contractor is to take all measurements for joinery works at the building, and not from the Interior Designer’s drawings, except where the work is specified to be “built in”.

FIXED-IN-JOINERY

Where joinery works are specified to be “fixed-in” or inserted in the positions, they are to occupy after the surrounding or enclosing carcass has been constructed.  It shall be the responsibility of the contractor to ensure that the necessary fixings are incorporated in the carcass.  Alternatively, the Contractor shall construct such ground works as are required to provide a suitable base and fixing for the joinery works.  The spaces enclosed in the ground works and behind joinery works, shall be filled in solid with plaster.  The Contractor is to secure “fixed-in” joinery works so that they are plumb and true to the shapes and dimensions shown on the working drawings and details.  Vertical junctions shall be solidly bedded with mortar, wedged or otherwise secured, as may be specified or as is most appropriate in the circumstances, but a clearance is to be maintained in all overhead junctions so that settlements in the building carcass may take place without stressing or otherwise loading the joinery works.

Joinery works shall not be fixed in position until after all floor, wall and ceiling surfaces have been formed or constructed, unless otherwise specified.

JOINERY ASSEMBLED IN-SITU

Where joinery works are specified to be “assembled in situ” and all stresses of support and fixing are to be engaged in the building, it shall be the responsibility of the Contractor to ensure that the necessary fixings are incorporated in the carcass; alternatively, the Contractor shall construct such ground works as are required to provide a suitable base and fixing for the joinery works.

The spaces enclosed in the ground works and behind the joinery works shall be filled in solid with plaster or weak concrete.

In situ joinery works shall not be executed until after all floor, wall and ceiling surfaces have been formed or constructed, unless otherwise specified.

DRAWINGS

Work is not the commence until the Interior Designer has approved the manufactured full-size setting out drawings to be provided by the Contractor.  Suggestions which the manufacturer may wish to make modifying the construction and joints shown on the Engineer’s drawings will be considered.

INSPECTION

Facilities are to be given for the Interior Designer to inspect all work in progress in shops and on the site.

TIME FOR DELIVERY

None of the joinery is to be delivered until it is required for fixing in the building.  Joinery which does not require to be built in as the work proceeds is not to be brought to the site and fixed until the building in enclosed.

TRANSPORT AND PROTECTION

The joinery is to be kept under a waterproof cover during transit and it is to be similarly covered and kept clear of the ground on the site.  It is to be handled and stacked carefully to avoid damage.

MAKE GOOD DEFECTIVE WORK

Should any shrinkage or warping occur or any other defects appear in the joiner’s work before the end of the defects liability period such defective work is to be taken down and renewed to the Interior Designer’s satisfaction and any work disturbed in consequence must be made good at the Contractor’s expense.  Should any shrinkage or warping occur or any defects appear, which cannot be rectified the Contractor shall remove such defective work and replace by new one at his own expense.

Electrical, Fire Alarm and Air Conditioning Works at Gokoolah Community Wellness Centre

SCOPE OF WORKS, SPECIFICATIONS AND PERFORMANCE REQUIREMENTS

PART A: GENERAL REQUIREMENTS OF ELECTRICAL & ALLIED WORKS

## GENERAL CLAUSES

The installation of electrical, fire alarm and air-conditioning equipment shall comply with the requirements described in this Technical Specifications. The clauses shall be applied homogeneously throughout the Specifications.

## APPLICATIONS

The installation shall comply in every respect with this Specification unless otherwise specified in the Particular Specifications, the Drawings and/or the Standard/Guidance Drawings relating to a particular job or modified by written instruction of the Project Manager or his representatives.

The Bidder should firstly check that he is in the possession of a complete set of Bidding Documents and by reference to index and content summary pages; he should ensure that all pages are in correct sequence and that none is missing. Any discrepancy or other irregularity should be notified to the Client immediately.

The Priced Activity Schedule (PAS) has been prepared with a view to provide a common basis for biding. Before submission of bid, it is deemed that the Bidder has acquainted himself with all conditions prevailing on site. All the Specifications, Priced Activity Schedule, Drawings are complementary and should be read accordingly. The Bidder is advised to carry out measurement and check the quantities of materials. In case of discrepancies, omissions or errors, the Bidder shall inform the Client prior to submission of the bid. No extra claim shall be entertained afterwards on this issue.

The Bidder is advised to read carefully these instructions and to ensure that he has complied therewith in all respects on submitting the bid.

## SCOPE OF WORKS

The scope of works shall consist of, but not limited to, the supply, installation, connection, testing and commissioning of the following:

- Electrical System

- Cables, including feeder cables and final wiring

- Wireways, including cable trays, cable ladders, conduits and trunkings

- Luminaires

- Accessories, including switches, sockets and hand dryers

- Distribution Boards and Switchgears

- Extract fans

- Fire Detection and Alarm (FDA) System

- Fire Alarm Panel

- Detection devices, including smoke detectors

- Manual Call Points

- Alarm devices, including sounders

- Fire retardant cables

- Air-Conditioning Systems

- Split AC Unit complete with support and piping

The contractor shall supply, install, test and commission Works and Equipment in the manner set out in the non-exhaustive specifications or where not set out, to the satisfaction of the Project Manager or his representatives and all reasonable variations on site shall be carried out in accordance with such directives as the Project Manager or his representativesmay give. It is to be understood that the project shall be completed for the fixed sum bided and accepted inclusive of any item which might not be mentioned in the Specifications, Priced Activity Schedules, Bill of Quantities / Breakdown of Contractor’s Price and Drawings but deemed necessary for the completion of the project and proper functioning of the System / Equipment.

## VOLTAGE COVERED BY THIS SPECIFICATION

Unless otherwise specified, all apparatus, equipment, materials and wiring shall be suitable for use with a Single Phase/Three-phase and neutral, 4-wire, 400/230 VAC ± 6%, 50 Hz.

## SITE VISIT

If site visit is not mandatory, bidder is advised to visit the site before submission of bid so as to be fully acquainted with the nature of the site and extent of work involved. Bidder shall contact the Client for site visit arrangement.

## INSTALLATION TO COMPLY WITH REGULATIONS

The electrical installation shall comply with the latest edition of the following statutory obligations and regulations together with any amendments made thereto:

- Code of Practice for the Electricity (Wiring) Regulations issued by the Mauritius Standards Bureau or BS7671:2018

- Electricity Act 2005

- Central Electricity Board Requirements

- IEC, ISO, EN, BS EN and BS

- Government Fire Services Requirements

- Code of Practice for Energy Efficiency of Electrical Installations

## SAFETY REQUIREMENTS

The electrical installation shall comply with all regulations on safety aspects issued by the followings:

- Occupational Safety and Health Act 2005 and Occupational Safety and Health Amendment Act 2009

- Manual issued by the Ministry of Labour, Industrial Relations and Employment

- IEC, ISO, EN, BS EN and BS.

## CASE OF CONFLICT

In case of conflict between the technical requirements of this Specification and any other requirements, the following order of preference shall apply, unless mentioned otherwise:

- Acts, Regulations and Guidelines of Local Authorities

- IEC, ISO, EN, BS EN and BS including Code of Practice for Electricity (Wiring) Regulations

- Contractual Clauses in Instruction to Bidders, Conditions of Contract and other related document, including Bid Data Sheet and Particular / Special Conditions of Contract.

- This Specification and the Standard/Guidance Drawings

Should the Bidder conclude from the bid document that there exists any inconsistency, discrepancy or conflict within the content thereof of figures and words indistinct or be in doubt as to the true meaning of any part of the Bidding Documents, he must notify the Client for clarification, prior to the submission of the bid.

## SITE EXIGENCIES

The selected Contractor shall respect security arrangements in force at the site/building and shall seek necessary permission and security pass for access, if any, for execution of the work. The Contractor shall carry out works outside normal office hours where deemed necessary and authorized by Client without any increase in contract cost. Claims for overtime works shall not be entertained. The site shall be kept tidy and no materials/refuse shall be kept which may cause obstructions.

Bidders are informed that their site of work is a building in operations with activities shall remain in operation during contract period. The removal of existing installation, if applicable and installation of new system must be carried out while maintaining continuity of service within the building.

Contractor to make appropriate arrangements with the Client concerning use of existing power and water supplies prior start of works. Toilet facilities will be provided subject to availability. Parking generally will not be provided during normal working hours and prior arrangements must be made for parking after normal working hours. Contractor should plan appropriately for loading and unloading of materials as well as debris for carting away.

Contractor shall provide necessary protection to the building structure and surroundings, existing equipment and furniture. He shall be responsible for making good any damage caused to the satisfaction of Client, without increase in Contract Price. Otherwise, these costs shall be deducted from amount due to the contractor.

Contractor shall provide proper security against work hazards. The bidder should submit a report on the working conditions by an experienced Safety and Health Officer, whenever required, without increase in Contract Price.

Any operation that may cause nuisance to the occupants of the building, appropriate arrangements must be made with the Client. Switching off of power supply shall be carried out only after normal working hours.

On particular days, Client may request the Contractor to stop all site works and the latter shall abide accordingly.

Therefore, Contractor shall take into account of working overtime or outside normal working hours, provision of additional workforce and resources in order to meet the schedule completion date. All works to be performed outside normal working hours must receive prior approval from the Client with regards to access and storage of materials.

Bidders shall include for all the above within their bid. Under no circumstances, the Contractor shall be entitled to extension of time except for valid reasons which he will prove and justify.

## MATERIALS & EQUIPMENT

Equipment/materials for this project shall be as per Specifications / Schedules or as indicated on the Drawings. Bidder shall specify clearly the Make and Model of various equipment/materials proposed. These shall be accompanied by original documentations, catalogues, samples (where requested), etc.

The decision of the Project Manager or his representatives shall always be final and no materials/equipment shall be supplied / installed in the project without approval.

## INTERNATIONAL STANDARDS

Material and equipment shall be of high quality, and shall comply with, where applicable, the appropriate International Standard Specifications prepared by IEC or ISO Technical Committees together with any amendments made thereto.

## OTHER STANDARD SPECIFICATIONS

When material or equipment complying with other international standard specifications is offered, the Contractor shall satisfy the Project Manager or his representatives that the quality of the equipment offered is equal to or better than that specified in the appropriate International Standards (IEC/ISO).

## THE INTERNATIONAL SYSTEM OF UNITS (SI)

The International System of Units (Système International d’ Unités) of weights and measures shall be used for all electrical materials and equipment.

## SELECTION OF EQUIPMENT

Selection of equipment shall be based on this Specification, the Particular Specification, and technical data contained on the Drawings for a particular installation.

Where items of equipment are interconnected to form an integral part of the complete installation, their characteristics of performance and capacities shall be so matched as to give safe, reliable, efficient and economical operation of the complete installation.

Whenever equipment is called for in the Particular Specifications or Drawings for the installation of a particular job, all this equipment shall conform to energy efficiency requirements.

## EQUIPMENT CATALOGUE AND MANUFACTURER’S SPECIFICATION

Equipment catalogues and manufacturers’ specifications related to the proposed equipment shall be in the English or French language, be specific and shall include all information necessary for the Project Manager or his representatives to ascertain that the equipment complies with this Specification and Drawings. Data and sales catalogue of a general nature will not be accepted.

Equipment catalogues and manufacturers’ specifications must be submitted for the examination and agreement of the Project Manager or his representatives before any equipment is ordered.

All proposed item shall be of reputable make; manufacturer should possess a valid ISO9001 or equivalent certificate. A copy may be requested during evaluation.

## WORKMANSHIP

### PERSONNEL

All work shall be carried out by or under the direct supervision of a CRPE Registered Engineer appointed by the Bidder.

All tradesmen shall be qualified and competent, and work under at least one experienced technician (minimum to be Diploma holder with three years’ experience in the trade) and the work carried out shall be consistent with the good practice in Mauritius and to the satisfaction of the Project Manager or his representatives.

Bidder may be requested to submit signed CVs with supporting evidence for academic and work experience claimed at post contract stage.

### TOOL AND INSTRUMENT

Proper tools shall be used for carrying out the electrical installations.

Calibrated, adequate and accurate testing/measuring instruments shall be used to demonstrate compliance of the electrical installations with the relevant specifications and regulations. The Project Manager or his representatives has the right to stop any work on which the correct tools and/or instruments are not being used.

## LABEL AND NOTICE

### INSCRIPTION OF LABEL AND ENGRAVING

Inscription of label and engraving shall be in English characters. Details shall be submitted to the Project Manager or his representatives for agreement prior to engraving. All switches, sockets and cooker units should have their own label.

### MATERIAL FOR LABEL

Label should be of white plastic with black or red lettering or printed on white tape engraved as required. Where distribution board is fitted with labels provided by the manufacturer of the distribution board, these labels may be used in lieu of the white plastic label provided that they are of equivalent quality and approved by the Project Manager or his representatives.

### FIXING OF LABEL

Label should be glued or fixed to switchgear and distribution board by screws, as instructed by Project Manager or his representatives.

### WARNING NOTICE

Warning notices shall be provided as required by Operational Health and Safety Act 2006 and its regulations. In addition, the following warning notices may be provided at the appropriate positions:

- A label having minimum size of 65 x 50mm marked with the words ‘DANGER - ELECTRICITY’ in not less than 5mm thickness of characters to be fixed on every container/enclosure of ancillary equipment operating at voltages exceeding “low voltage”.

- A label having minimum height 30mm marked with the words ‘TWO SOURCES OF POWER SUPPLY’ in not less than 5mm thickness of characters to be fixed on SDB1.

- A label to be fixed in such a position that any person gaining access to the live parts of an item of equipment or enclosure, which are not capable of being isolated by a single device and not provided with an interlocking arrangement to isolate all circuits concerned, will be adequately warned of the need of taking special precautionary measures to use the appropriate isolating devices.

### OTHER LABELS AND NOTICES

Other labels and notices shall be provided where appropriate.

# PART B: ELECTRICAL SYSTEM

## ENCLOSURES

Enclosures should include all necessary components and accessories to form a complete assembly which should be firmly fixed in position in the enclosure. Ample space should be allowed for cabling. Enclosures shall be sized to allow minimum 15% of spare capacity.

Switchgears should be arranged neatly in rows.  All components should be totally concealed with only the toggles should protrude through the cover plate of the distribution board. The required characteristics are as follows:

Type A

- Reinforced Polyester or fiberglass

- Conform to IEC 60529 or equivalent

- Wall mounted

- Hinged transparent or plain door

- Fitted with chassis and standard DIN Rails

- Adequate natural / forced ventilation

Type B

- Reinforced polystyrene enclosure with polycarbonate door

- Conform to IEC 60670 or equivalent

- Class II, IP40 with door and faceplates

- Self-extinguishing type

- Wall mounted

## SWITCHGEARS

## MINIATURE CIRCUIT BREAKER

Miniature Circuit Breaker (MCB) should be to BSEN 60898, designed for installation on standard profile DIN EN50, 022 rails or screw fixing on mounting plate. Number of poles should be according to as mentioned in schematic diagrams.

The Contractor should ensure that breaking capacities of the switchgear proposed match the requirements of the installation (Minimum 10kA on header and 4.5/6kA on final circuits).

## RESIDUAL CURRENT DEVICES

Residual Current Devices should be to BSEN 61008 / BSEN 61009 with rated residual operating current of 30mA, unless indicated otherwise.

## SURGE ARRESTER

It should be modular type with the following characteristics:

| Voltage Rating/Frequency | 200 - 240 Vrms/4763 Hz |
| --- | --- |
| Nominal Discharge Current/ph | 15 kA 8/20µs one time |
| Follow Current Extinguishing capability/ph | 50 kArms |
| Response Time | <100 ns |
| Let through Voltage at | 700 V Ph/N 3 kA 8/20 µs one time |
|  | 700 V Ph/E |
| Protection level | 5.0 kV at In |
| Lifetime indicator | Yes |
| Suitable for Neutral point connections | EEENIE |
| Standard | Type 2 IEC 61643-11 |

## LUMINAIRES

Luminaires should comply with BS 4533 / EN 60598 or other recognized European standards and has certification from recognized certification body such as CE, RoHS or FCC. All luminaires shall preferably comply with IEC61000-3-2. Bidder may be required to produce evidence of certification. Wherever applicable, luminaires should be secured to wall or roof using fisher plug or corrosion resistant rawl bolt or similar; rawl plug is not acceptable.

GENERAL REQUIREMENTS OF LED LUMINAIRES

The luminaire should be rated at 230V a.c. ± 6%, 50 Hz with minimum power factor of 0.9 and minimum Correlated Colour Temperature (CCT) of 4000K, except if stated otherwise. The luminaire must be manufactured to British standards or equivalent European standards. The luminaire must be marked with a full production catalogue number that matches manufacturer documentation. A full sheet of product specifications should be submitted with compliance certificates. Following data should be provided:

- Power (W);

- Luminous flux (lm);

- Luminaire efficacy (lm/W);

- Correlated Colour Temperature (CCT);

- Colour Rendering Index (CRI)

A sample of the complete luminaire may be requested from the bidders during evaluation of the bids, unless specified as mandatory submission during bidding, or approval of materials. The luminaire should be constructed from corrosion resistant materials such that no undue deterioration occurs in its safety, performance or appearance during normal life when operating under all local conditions.

The optics of the LED luminaire should be of toughened glass or moulded polycarbonate. The entire housing (both LED section and Driver section) should be dust and water proof. Parts constructed of Polycarbonate should be UV stabilized (lens discoloration will be considered a failure under warranty).

Operating temperatures should be from 10° C to 40° C on the housing (case temperature). Operating humidity should be up to 90%. The unit should be EMC compliant to the EN55015 or EN6147-1 standard.

The luminaire should be completely pre-wired, requiring only the connection of the electrical power supply cables to the terminal block. The LED Module should have the following features:

- Heat sink with high thermal dissipation properties;

- Corrosion resistant;

- Diffuser should be UV protected;

- Operate in relative humidity of 80% or better

- Constant current driven

The rated LED life should be at least 20,000 hours, unless stated otherwise, with LED operating at (Ta) 35°C.

### TYPE A: LED Panel

LED Panels should be of the following features:

- Luminaires 600 x 600 LED Panel suitable for false ceiling

- Daylight

- Power factor 0.98

- Polycarbonate diffuser and steel/polycarbonate white body

- Similar to DIETAL RAPSODY

### TYPE B: Indoor Wall Lamp

Indoor wall lamps should be of the following specifications:

- Metal with brass finish or Brass body with antique aesthetics

- Transparent glass diffuser

- Around 250mm High x 150mm Wide and 200mm Deep

- One or two E27 lamp holder and E27 LED lamp of reputable make

### TYPE C: Outdoor/Stairs Wall Lamp

Wall lamp to be used outdoor and stairs should be of the following specifications:

- Wall mounted bulkhead complete with LED lamp of reputable make

- IP55, Class II insulation minimum

- Minimum impact resistant of 20J

- Circular/Oval with fiberglass reinforced polyamide body

- Diffuser should be of molded opal polycarbonate and anti-UV with sealing system incorporated

- Reflector should be aluminium with polycarbonate diffuser

- Ring finish should be white without grill

### TYPE D: Waterproof Luminaires

Weatherproof luminaires should be of the following features:

- Length: 4 feet

- LED type

- Watertight to minimum IP 65, vandal proof and impact resistant

- Linear composite body with fibreglass reinforcement, saturation dyed and UV stable

- White pre-lacquered sheet steel forming reflector

- Diffuser to be of injection-moulded polycarbonate with interior prisms and smooth flexible exterior.

- Mounting clips to be of stainless steel.

### TYPE E: LED Spot Lights

LED Spot Lights should be of the following features:

Type E1

- Spot Light LED (3 W) with aluminium reflector suitable for landscape

- Warm White

- Power Supply - 230VAC/50Hz

- Aluminium body

- IP55

Type E2

- Recessed Spot Light LED (3 W) with aluminium reflector

- Approx. size diameter (70-100 mm)

- Warm White

- Power Supply - 230VAC/50Hz

### TYPE F: Ceiling Lamps

Ceiling lamps should be of the following features:

- Ceiling mounted bulkhead complete with LED lamp of reputable make

- IP55, Class II insulation minimum

- Minimum impact resistant of 20J

- Fiberglass reinforced polyamide body

- Diffuser should be of molded opal polycarbonate and anti-UV with sealing system incorporated

- Reflector should be aluminium with polycarbonate diffuser

- Ring finish should be white without grill

### TYPE G: LED Floodlight

LED floodlights of reputable make should be rated IP55, 100W minimum.

The floodlight should be of wide beam type (Beam angle ≥100°) suitable for outdoor use and landscape lighting.

### TYPE H: Chandelier

Chandelier should be of the following features:

- Ceiling mounted

- Brass body or metal with brass finish and golden appearance

- Minimum of 6 Nos x E27 lampholder and E27 LED lamp of reputable make

- Glass with crystal pendants

The successful bidder is required to quote for its suspension support and wiring. Successful bidder shall submit proposals during execution of work with the best quote. Same will be met from provisional sum. Client reserves the right not to accept any of the proposed chandeliers and supply one to the successful bidder for installation.

### TYPE I: Landscape Wall Lamp

Landscape Wall Lamp to be used in the green space should be of the following specifications:

- Wall mounted complete with LED lamp of reputable make

- IP55, Class II insulation minimum

- Minimum impact resistant of 20J

- Fiberglass reinforced polyamide body

- Diffuser should be of molded opal polycarbonate and anti-UV with sealing system incorporated

- Reflector should be aluminium with polycarbonate diffuser

- Ring finish should be white without grill

### TYPE J: EMERGENCY/EXIT LIGHTS

Emergency/Exit lights shall be to the following specifications:

- Self-Contained and non-maintained with at least 2 hours’ operation

- Self-Test

- Suitable for ceiling/wall mounting

- LED lamp (minimum 3W)

- Polycarbonate body

- Sealed Nickel Cadmium Battery

### TYPE K: POLE LIGHTS

- These columns shall comply with BSEN40. They shall be of steel tubular section octagonal taper type, height not less than 6m with high quality hot dipped galvanised finish to withstand marine conditions. The thickness of galvanisation shall be at least 60 microns on both sides (inside & outside) of the pole to BSEN ISO 1461 , BS 3987 and BS EN 12373.

- The columns shall be formed out of galvanised steel of thickness not less than 4mm to afford an axial weld only; circumferential weld shall not be permitted. The top of the pole shall be plugged to prevent ingress of water and dust.

- The columns shall be provided with a flanged baseplate surface mounted with approved anchor bolts and two nuts per bolt. Holding down bolts shall be supplied with necessary templates before foundations are formed. The base of the pole (across flats) shall not be less than 250 mm or as directed.

- All metallic accessories shall be hot dipped galvanised. The column with 1 No. lantern (Single Bracket) shall be capable to withstand sustained wind velocity of 300km/hr.

- Concrete Base for Pole: The poles shall be erected on concrete bases of appropriate dimensions and complete with suitable reinforcements.  The bidder shall provide details of dimensions and steel armouring of concrete bases such that the column shall withstand a wind velocity of 300 km/h when completely installed (and equipped) on site.

Successful bidder shall submit signed design for pole and base from a CRPE Registered structural Engineer prior to commencement of production. A written guarantee shall be submitted to this effect during commissioning. The guarantee shall also cover anchor bolts and nuts.

- The luminaire should generally feature the following:

- Suitable for landscape lighting applications

- Operating power: 230V/50Hz

- Light fitting power:  Minimum 250 W

- LED luminuous efficiency: at least 110 lm/W

- Angle of diffusion: at least 120 degrees

- Color Temperature: at least 4000 K

- Color Rendering Index:  ≥70

- Housing Material:  Aluminum

- Reflector material:  Polycarbonate

- Optic material:  Polycarbonate

- Optical cover/lens material:  Polycarbonate/Alumunium

- Fixation material:  Aluminum

- Mounting device:  Mounting bracket adjustable

- Optical cover/lens finish:  Clear

- IP  protection: IP66

- Mechanical. impact protection: IK08

- LED Lifespan: at least 50,000 hours

- Insulation Class I/II

- Manufactured to European Standards

## CABLE WAYS

Cables should comply with BS 6500 and IEC 60502. Cables should be of 600V/1kV grading conductors of high conductivity copper wires.

Colour code of cable should be as follows:

| First phase (L1) | Brown |
| --- | --- |
| Second phase (L2) | Black |
| Third phase (L3) | Grey |
| Neutral (N) | Blue |
| Earthing (E) | Yellow-Green |

The cables should be routed mostly in cable trays, fire-retardant trunking, conduits or as specified. The cables should be neatly grouped without any crossing and should be properly clipped at recommended interval of 1 metre and at bends. All cabling should be complete with end terminations, cable glands, lugs, etc. Bending radii of cables should conform to British Standards.

Wiring for final circuits should, unless otherwise specified, be carried out in non-armoured 1kV grade single-core PVC- insulated cables manufactured in accordance with BS 6004 / BSEN 50525. Cables should be stranded copper conductor and self-coloured insulation to BS 6746.

No cables or cable way shall rest on the false ceiling. The Successful bidder shall plan appropriate way to run the cables in ceiling using cable tray, conduit and junction boxes prior to erection of false ceiling. If any cable or cable way found laid on the false ceiling during commissioning or defects liability period, the successful bidder shall remedy same, and any damage caused, without extra cost.

## TRUNKING/CONDUIT

All single core cables should be within fire retardant trunking or PVC conduits. Within the conduit, circuits should be bunched at reasonable intervals and should be properly labelled. They should be supplied with cable straps at 2000mm intervals. Inspection boxes should be provided to allow for periodic inspections and maintenance works.

Conduits of adequate dimension should be used in order to satisfy cable space factor. Manufacturer’s standard fittings (e.g., bends, tees, end plates) should be preferably used throughout.

White PVC conduit should be used on exterior surface of buildings or above false ceiling. Conduit of adequate dimension should be used in order to satisfy cable space factor. These should be securely fixed using saddles, copper screws and rawl plug at regular 500mm intervals.

## EARTHING

The Earth Resistance and Loop Impedance shall be as per BS7671. A minimum of three earth rods of diameter 20mm or more and length 1000mm or more shall be installed with respective inspection pits. The drawing below shows a proposed earthing method.

MAIN DISTRIBUTION BOARD           (MDB)

Single-Core 16 mm2

Rigid Copper Earth Conductor

EARTH PIT

EARTH PIT

EARTH PIT

4000 mm

5000 mm

Min Ø20mm, 1000mm long, earth rod

EARTH PIT

5000 mm

Copper Earth Plate 600mmx600mmx 3mm

(Optional)

Note:

The distance and number of earth rods and earth plates shown is indicative only.  Additional earth rods and earth plates should be added (if necessary) until the desired value of Earth Resistance is obtained.

CONCRETE EARTH PIT

CLAMP

Interconnecting Earth Conductor Single-Core Copper 16 mm2

Copper Rod: Min 1000mm, Ø20mm

Cover (removable only by tool)

Surface Soil Level

500mm

Concrete Earth Pit

Rock free soil/ Soft Soil

Surface Level +0.00

Underground Electric Cable as per given specifications inside Yellow PVC Sleeve

(One shown typically – minimum clearance of 25mm between sleeves)

Yellow Warning tape written “DANGER ELECTRICITY”

Compacted Rocksand

Approx. 600mm

300 - 500mm

750mm

300mm

Details of Underground Cable Trench

## Manholes

Manholes (Electrical Draw pits) shall be built with reinforced concrete. Openings of sufficient size shall be made on the sides for entry of PVC pipes. The manholes shall have waterproof galvanised medium duty metal covers on top of which shall be marked “DANGER ELECTRICITY”.  All opening shall be properly sealed to prevent ingress of water, dust and rodents.

## HAND DRYER

Hand dryer shall be installed to the following specifications:

- Rating: Approx. 1.5 kW, 230V, 50Hz

- Fan: highly efficient and low noise fan

- Automatic “no touch” start and stop

- Drying cycle: Approx. 25 Seconds

- Safety features:

  - fitted with safety devices to protect heating unit and fan motor against overloading

  - fitted with timer to prevent the drier running continuously in the event of the sensors becoming obstructed

- Outer case: Preferably s/steel

- Anti-bacterial type

## EXTRACT FAN

Extractor Fans shall be to the following specifications:

- Wall /glass mounted with dimensions 200 mm

- Steel protected by polyester spray paint or High impact resistant thermoplastics

- Single phase 230 V, 50 Hz

- Air flow rate around 150 m3/h

- Motor/electrical connection protected to IP 55

- Automatic external shutters to prevent ingress of water

- Prevention of Back Draft

- Easily removable safety grille for maintenance/servicing

- Noise level shall not be greater than 50 dBA at 1 metre.

## SCHEDULE OF MATERIALS

The Bidder is required to complete this table stating the make, reference and origin of equipment/materials he intends to use for executing the Work.

| Description | Make / Country of Origin | Model | Reference |
| --- | --- | --- | --- |
| Distribution Board Type A |  |  |  |
| Distribution Board Type B |  |  |  |
| MCB |  |  |  |
| RCD |  |  |  |
| Isolator |  |  |  |
| Multi-core cable |  |  |  |
| Single Core Cable |  |  |  |
| Cable Tray |  |  |  |
| Trunking/Conduit |  |  |  |
| Luminaire Type A (LED Panel) |  |  |  |
| Luminaire Type B (Indoor Wall Lamp) |  |  |  |
| Luminaire Type C (Outdoor Wall Lamp) |  |  |  |
| Luminaire Type D (Waterproof 4ft) |  |  |  |
| Luminaire Type E1 (LED Landscape Spot Lights) |  |  |  |
| Luminaire Type E2 (LED Spot Lights) |  |  |  |
| Luminaire Type F (Ceiling Lamps) |  |  |  |
| Luminaire Type G (LED Floodlight) |  |  |  |
| Luminaire Type I (Landscape Wall Lamp) |  |  |  |
| Luminaire Type J (Emergency Light) |  |  |  |
| Luminaire Type K (Pole Light) |  |  |  |
| Switch / DP Switch |  |  |  |
| Sockets / Waterproof Sockets |  |  |  |
| Hand Dryer |  |  |  |
| Extract Fan |  |  |  |

Bidder to submit catalogues and full technical specifications of proposed equipment with the Bid. Proposed materials shall be of reputable make – manufacturer should possess a valid ISO9001 or equivalent certification. Client may request necessary documentation to validate the manufacturer’s reputation.

# PART C: FIRE DETECTION AND ALARM SYSTEM

## GENERAL

The proposed system should be inclusive of the installation, testing and commissioning of equipment and associated items for a complete Fire Detection & Alarm System. The system of addressable type shall be made up as follows:

- A combination of optical smoke/heat detectors and Manual Call Points to give alarms

- The detector or call point zone from which an alarm or fault originate shall be identifiable.

- A main control and alarm indicating panel with mimic diagrams and capable of indicating from which point the alarm emanates.

- Sounders to give audible alerts

## FIRE ALARM PANEL

The main panel shall comply with BS 5839. It shall addressable type with the following features:

- Walk test facility

- Monitored outputs

- Integral power supplied to provide power in case of mains failure (Maintenance free batteries lead acid type and charger)

- Surface mounting

- Integral call point and sounder

- Microprocessor based modular design

The panels shall have the following indications/operations:

- Fire Alarm - Maintenance alarm

- Device fault

- System faulty

- Auto reset

- Test mode

- Supply fault …etc

## POWER SUPPLY

The battery unit shall be capable to sustaining the normal load of the alarm system for a period of 10 hours, followed by the load of all sounders for a period of 45 minutes.  It shall comply with BS 5839 and shall include the following features:

- Have enough space for batteries

- Protection for battery/regulator circuits

- Reverse polarity protection

- Wall mounting

- Automatic battery load set

- Sealed lead acid batteries

The power supply shall also incorporate the appropriate charging circuit.

## DETECTION DEVICES

Manual call point to be compatible to BS 5839 and shall be of plastic cover and comply with following specifications:

- Push to membrane type with polycarbonate cover

- Shall have LED indication

- Recessed/surface mounting

- Shall be to IP 54 with weather resistant gasket.

Heat/Smoke detectors shall be to BS 5445 Part 7 and comply with the following:

- Pulse light source

- Pulses to trigger alarm

## ALARM DEVICES

Electronic Sounders shall be to the following specifications:

- Vandal proof

- Shall be to IP 55

- Shall be operated on 240V AC

- Sound output:  85 dB at 1m or 5dB above background noise with adjustable feature

## SCHEDULE OF MATERIALS

The Bidder is required to complete this table stating the make, reference and origin of equipment/materials he intends to use for executing the Work.

| Description | Make / Country of Origin | Model | Reference |
| --- | --- | --- | --- |
| Fire Alarm Panel |  |  |  |
| Heat/Smoke Detector |  |  |  |
| Fire retardant cables |  |  |  |
| Sounder |  |  |  |

Bidder to submit catalogues and full technical specifications of proposed equipment with the Bid. Proposed materials shall be of reputable make – manufacturer should possess a valid ISO9001 or equivalent certification. Client may request necessary documentation to validate the manufacturer’s reputation.

# PART D: MECHANICAL VENTILATION AND AIR-CONDITIONING SYSTEM

- GENERAL INSTRUCTIONS

- All tools required for the successful installation of the unit should be provided by the bidder including support, ladder, scaffolding, flaring tool and pressure gauges.

- All testing equipment should be provided by the bidder during commissioning including decibel meter, thermometer, pressure gauges, clamp meters and multi-meters. The Client or his representatives have the right to refuse the use of unbranded / non-calibrated tools. The bidder is responsible to provide a replacement without additional cost.

- Bidder should allow for suitable slope for the PVC drain pipes and run the pipes neatly on the inside / outside wall and false ceiling until the nearest drain. Bidder shall not modify any rainwater pipe without Client’s approval or terminate the drain pipe in flower pot. The drain pipe should be insulated at any place where there is a risk of condensation that may affect equipment or people. The drain pipe should be secured around 600mm interval of appropriate dimension considering insulation thickness.

- Copper pipes should be sized as per manufacturer’s recommendations and enclosed with good quality thermal insulation. The connection should be vapour sealed.

- Valves should be provided to allow for safe isolation of indoor and outdoor units without loss of refrigerant.

- Piping should be enclosed in white trunking or cable trays which is fixed at 500mm interval. The workmanship should be good and the use of trunking accessories (interior angle, exterior angle, endcap and joints) is highly recommended. Client or his representatives may not commission the equipment if the workmanship is poor.

- Bidder should drill concrete wall for the installation of the units. The hole should be sealed properly to avoid ingress of rainwater with foam or other suitable material.

- Bidder is required to produce three copies of test certificates.

- Bidder to put sticker on the outdoor unit indicating the date of successful commissioning.

- Bidder to put sticker on indoor unit indicating the date of successful commissioning and scheduled maintenance including technician’s name.

- SPLIT AIR-CONDITIONERS

  - ROOM DETAILS

| AC No. | Room | Type | Qty | Proposed Rating (BTU/Hr) |
| --- | --- | --- | --- | --- |
| 1 | Office | Wall | 1 | 12,000 |
| 2 | Server Room | Wall | 1 | 12,000 |
| 3 | Server Room | Wall | 1 | 12,000 |
| 4 | Hall | Ceiling | 1 | 36,000 |
| 5 | Hall | Ceiling | 1 | 36,000 |
| 6 | Hall | Ceiling | 1 | 36,000 |
| 7 | Hall | Ceiling | 1 | 36,000 |

  - GENERAL REQUIREMENTS OF SPLIT AIR-CONDITIONERS

Bidder to fill table below for each proposed make. If the bidder intends to propose more than two makes, separate sheets should be submitted. Bidder to fill table below for each proposed make. Bidder is advised not to propose more than two makes for each type of Split AC, else separate sheets should be submitted.

| Description | Requirements | Bidder’s Proposal |  |
| --- | --- | --- | --- |
| Make | To Specify |  |  |
| Technology | Inverter |  |  |
| Refrigerant | CFC Free (R22 not acceptable) |  |  |
| Power Supply | 400V/230V a.c. / 50Hz |  |  |
| Features | Dehumidification Auto-restart |  |  |
| Indoor Unit |  |  |  |
| Air Filter | Removable and washable |  |  |
| Display | Temperature in degree Celsius (ºC) |  |  |
| Louvers | Orientable Swing mode Remote controlled |  |  |
| Fan | Auto and manual Remote controlled |  |  |
| Intake | Fresh air intake hole |  |  |
| Outdoor Unit |  |  |  |
| Compressor | Rotary Hermetic preferably Inverter driven |  |  |
| Weathering | Suitable for tropical climates |  |  |
| Condenser fins | Corrosion proof |  |  |
| Brackets | Hot dipped galvanized |  |  |
| Other |  |  |  |
| Energy Class | B or better |  |  |
| Warranty on compressor | 3 years |  |  |
| Warranty on workmanship | 1 year |  |  |
| Warranty on Spare Parts incl. Indoor and Outdoor Printed Circuit Boards and communication boards | 2 years |  |  |
| Free maintenance post commissioning on a quarterly basis | 1 year |  |  |
| Copy of technical data (Manufacturer’s data sheet) | To enclose Original or Readable Copy |  |  |
| Deliverables | Operation and Maintenance Manual Remote Control Warranty Cards |  |  |

  - SPECIFIC REQUIREMENTS OF SPLIT AIR-CONDITIONERS

| Description | Requirements | Bidder’s Proposal |  |
| --- | --- | --- | --- |
| Capacity | 12,000 BTU/Hr |  |  |
| Type | Wall |  |  |
| Make | To specify |  |  |
| Model | To specify |  |  |
| Country of Origin | To specify |  |  |
| Rated Current / Power Consumption | To specify |  |  |
| Indoor Unit |  |  |  |
| Location of unit | As per drawing |  |  |
| Noise Level at 1m (High Fan) | Less than 52dB(A) |  |  |
| Outdoor Unit |  |  |  |
| Location of unit | As per drawing |  |  |
| Noise Level | Less than 60dB(A) |  |  |

| Description | Requirements | Bidder’s Proposal |  |
| --- | --- | --- | --- |
| Capacity | 36,000 BTU/Hr |  |  |
| Type | Ceiling |  |  |
| Make | To specify |  |  |
| Model | To specify |  |  |
| Country of Origin | To specify |  |  |
| Rated Current / Power Consumption | To specify |  |  |
| Indoor Unit |  |  |  |
| Location of unit | As per drawing |  |  |
| Noise Level at 1m (High Fan) | Less than 62dB(A) |  |  |
| Outdoor Unit |  |  |  |
| Location of unit | As per drawing |  |  |
| Noise Level | Less than 70dB(A) |  |  |

  - EQUIPMENT INSTALLATION

- The Contractor shall have to undertake the electrical installations from the Outdoor Unit to the DB via a distribution board with isolators/MCBs for each outdoor unit. The electrical wiring and control wiring from the indoor unit to the outdoor unit shall be enclosed within a separate white trunking of suitable dimensions and securely fixed to the wall.

- The Contractor is expected to execute a very good trunking work. Cables and piping should be enclosed in a cable tray.

- All the refrigerant pipes (which be vapour sealed) shall be thermally insulated inside and outside the building. All exposed piping outside the building shall be coated with appropriate plaster membrane or aluminium tape to avoid damage the insulation by birds or rodents.

- The Indoor Units shall be provided with suitable drainpipes, with sufficient slope for drain. The drainpipes shall be leak proof and be securely fixed as and where required on the wall inside and outside the building. U-trap shall be used, where necessary.

- The Air-Conditioner shall be equipped with remote control by means of which the Air-Conditioners may be switched on and off, the temperature and fan speed may be controlled and from which one may read the temperature via an LCD display.

  - CIVIL AND ASSOCIATED WORKS

- The installation of the Air-Conditioners necessitates civil works including painting and masonry works (drilling of a hole in order to pass the pipes) and/or modification of window panes/frames/metal work which shall be undertaken by the successful bidder.

- Any opening shall be properly sealed in order to avoid leakage or loss of cool air. All broken surfaces for installation of air conditioner must be made good by the Contractor including paint and decorative works.

- Any supports, mounting brackets, cable tray etc… shall be supplied and installed by the Contractor.

- All necessary civil and plumbing works shall be included in the quotation, and shall be undertaken by the Contractor.

- Any support, ladder, scaffolding, tools and equipment required for installation must be provided by the Contractor.

  - WARRANTY

- The compressor of the Air-Conditioner shall have warranty for a period of 3 years and all other parts (including electronics card) shall have warranty for a period of 2 years. These warranty periods shall be effective only as from the date of successful commissioning of the Air Conditioner.

- Free maintenance on a quarterly basis and one yearly general servicing shall be provided during the one-year warranty/defect liability period. Repair works to the equipment during Warranty/Maintenance period shall be completely free of charge or included in the rate of the air conditioner and shall include spare parts, labour, gas charging, tools, transport, and any other items required. Quarterly report must be submitted.

- No claim whatsoever for servicing, maintenance, repair works, spare parts, labour, gas charging, tools, transport, or any other items will be considered during the Warranty/Maintenance period, unless exceptional cases.

  - AIR CURTAINS

Air curtains shall be of the following technical specifications:

- Wall/Ceiliing mounted

- Noise level: 55 dBA at 1 metre at high speed

- Variable fan speed control

- Wireless remote control

- Vertical air flow (around 25 m3/min) with orientable air deflection

- Operation Air Velocity around 10 m/s at 3 metres

- Length of air curtain: 1200mm

- Efficient, Compact & Elegant Design

- Reputable Make

| Description | Make / Country of Origin | Model | Reference |
| --- | --- | --- | --- |
| Air Curtain |  |  |  |

Bidder to submit catalogues and full technical specifications of proposed equipment with the Bid. Proposed materials shall be of reputable make – manufacturer should possess a valid ISO9001 or equivalent certification. Client may request necessary documentation to validate the manufacturer’s reputation.

# PART F: HANDING OVER

- GENERAL

After the system is practically installed with all accessories, components, spares, training and tools provided complete with satisfactory testing and all drawings, instructions, charts and maintenance manuals are provided, the system must therefore be commissioned and handover to the Client.

- TESTS

The Contractor shall ensure that each part of the installation is intrinsically safe and properly isolated. On completion of the installations, the Contractor shall carry out tests in the presence of Project Manager or his representatives. The following tests shall be performed as a minimum:

- Earth impedance test

- Insulation resistance of all cables.

- Earth resistance test.

- Polarity test.

- Continuity tests

- Operation of protective devices

- RCD tripping time

- Load test

- Fire Detection & Alarm Tests

- Mechanical Ventilation and Air Conditioning Tests

Arrangements for testing including supply of test equipment shall be the responsibility of the Contractor. Test and measuring equipment used shall be of good quality.

- MAINTENANCE MANUAL

The Contractor shall submit three (3) copies of Manual and Test Certificates for the installed system. The manual shall preferably be of A4 paper size with stiff plasticized cover and coloured cover for each sub-section and easy-referenced detailed index.

The manual shall include all operating, certificates and maintenance instructions for the equipment installed with the following, where applicable:

- Plant with nameplate details

- Legend of colour coding of all services

- Internal wiring diagrams of equipment and panels

- Procedures for fault finding

- Procedures to adopt if an item fail in its operation

- Itemized list of all essential and secondary spares

- Index of all drawings

- Records of performance tests

- Switchgear

- Other systems not mentioned here but relevant to present job.

The manual may contain all details relating to manufacturer (standard operating and maintenance instructions or leaflets). Where the equipment is non-standard, the manufacturer shall give information for the manual. “Hand-out” cards supplied by the manufacturer with the equipment shall be fixed to walls adjacent to the equipment.

- DRAWINGS

Throughout the progress of works, information necessary for preparing the drawings shall be recorded accordingly. Progress drawings shall be made available for inspection and checking upon request.

The drawings shall illustrate the following:

- Position of all equipment

- Sizes, types and routes of all cables and conduits

- Reference number of all circuits and accessories.

All drawings must be submitted for approval to the Project Manager or his representatives and thereafter the following set shall be provided:

- Complete set of drawing on approved plastic material

- Two (2) complete set of as-made prints on paper

- One set of all drawings shall be provided on writable 32GB USB pen drive. This set must be in editable format. Soft copies of the equipment’s manual and operational information should be provided.

The complete set including manual shall be signed by a Registered CRPE Engineer.

Scope of works and specifications for Mechanical works

for Proposed New Community Wellness Centre at

Gokoola

1.1.	INTRODUCTION

•	The project consists of construction of a single storey Wellness Centre at Gokhoola.

•	The Mechanical services have been designed to comply with all local regulations and by laws as far as possible. Where specified, the building shall comply to some sections of the British Standards and the Guidelines published by the local Authority.

•	Any approval, check, certificate, consent, inspection, instruction, proposal, request, test, or similar act by the Engineer (including absence of disapproval) shall not relieve the Contractor from any responsibility he has under the Contract, including responsibility for errors, omissions, discrepancies and non-compliances and the responsibility to provide a complete installation fit for its purpose-the purpose being a building for the provision of healthcare to the public.

•	This specification sets out the standards of materials and workmanship for the project. All materials shall comply with the latest European Standards or the Standards specified elsewhere in the Sections / Drawings or price activity schedule.

•	The installation shall include for all aspect of Health and Safety for those who are going to operate and maintain the installation.

1.2.	SCOPE OF WORK

The contractor shall be responsible to supply, install, test and commission the following services:

o	Cold water distribution system

o	Drainage system (Above ground and below ground)

o	Portable fire extinguisher

1.3.	SERVICES DESCRIPTION

1.3.1.	Cold Water Distribution System

•	Water to the site shall be provided from the existing CWA main.

•	Water for domestic purpose shall be stored in a fiberglass water tank located on site which shall subsequently be transferred to water tanks on the roof of each building.

•	 A domestic water pump shall be used to transfer water to the roof water tank as well as supplying pressurised water to the sanitary wares.

•	Water to sanitary wares shall be supplied by a combination of gravity and pressurised using uPVC pipe where surface mounted and HDPE pipe where buried.

•	All distribution pipework shall be in pressure rated uPVC PN16 where surface mounted and HDPE PN 16 where buried. The Contractor shall terminate all cold water services to sanitary wares as required.

•	Cross linked polyethylene pipe (PEX) pipe enclosed inside sleeve shall generally be used for final connection to sanitary wares.

•	Concrete base shall be provided to support pipes on roof

•	Angle valve shall be provided at the pipe inlet for each sanitary.

•	Trenches as detailed in drawings shall be provided for the buried pipe

1.3.2.	Drainage

•	Foul drainage from the building shall be disposed on site via septic tank and leaching field.

•	Waste from the existing building shall be diverted to the new septic tank as shown in drawings.

•	All waste pipes shall terminate to gully traps located on site prior to discharge/ connection to the soil network. All soil, waste and ventilation pipework shall be in uPVC.

•	Grease trap shall be provided at the back of the kitchenette.

•	Cover for all gully trap, manholes and inspection chamber shall be made of cast iron.

•	The Contractor shall provide the soil, waste and vent system, as necessary, to serve the sanitary ware provided, including terminating services to the sanitary ware.

•	Trenches shall be provided for the buried pipe.

•	The contractor shall be responsible to undertake survey of the existing manholes, measure level where required and include same in the shop drawings.

1.3.3.	Portable fire extinguisher

•	A combination of carbon dioxide and ABC powder portable shall be provided across the building that shall be used as a first aid firefighting purpose.

•	The extinguisher shall be wall mounted and activated manually.

2.	COLD WATER SERVICES

2.1.	      Cold water distribution system

•	Pipes, valves and fittings shall be selected to suit the different requirements of the service as shown on the drawings and comply with both the Central Water Authority & European standard where applicable.

•	All cold water services shall be classed as potable.

2.1.1.	              Pressure Testing

•	Shall be generally to BS 6700 and shall be carried out after a preliminary inspection for leakage with the pipework full of water at normal pressure.

•	Shall be applied to completed sections of pipework and finally to the whole installation and comprise the following hydraulic pressures which must be held for not less than twenty four hours after the rectification of any leakages: -

Distribution Pipework

Test Pressure= Twice maximum static head or 6 bar.g whichever is greater.

Note: Contractor to ensure that pressure test shall be lower than the pressure rating of the pipe.

2.2.	Quality of Installation

•	Installations shall be to specification and comprise new materials assembled to a high standard of workmanship under the supervision of qualified personnel. The following clauses list examples of materials and work that will be rejected: -

•	The use of damaged parts and incorrect types, standard, sizes, materials, markings, etc.

•	Damage to parts by tools, soldering, brazing, welding, etc.

•	Pipes not cut clean and square with the axis or removed of burrs, or pipes cut with bevel wheel cutters.

•	Pipes or fittings with broken or damaged threads

•	Joints misaligned or distorted and not true with pipe axis.

•	Pipework runs without the required gradient.

•	Pipes supported from other pipes or not capable of individual removal without disturbing other pipes.

•	Misaligned or distorted supports, fixings and pipework.

•	Insecure supports or restrictive of proper expansion, contraction, or lateral movement as required for the pipeline, or branch pipes used as supports for risers.

•	Pipes supported on the sleeve of fire stopping, or the fire 	stopping not fitted correctly or to the required standard.

•	Bores of pipes and fittings which are blocked or contaminated by foreign matter.

•	Eccentric fittings assembled the wrong way up-the taper should rise in the direction of flow.

•	Valves difficult for access for operation or maintenance.

•	Any items not installed to manufacturers recommendations.

•	Inadequate protection against electrolytic action.

•	Other faults may also apply including any disclosed by weld inspections, testing and commissioning.

2.3.	Pipe Ends and Cutting

•	Pipes shall be cut clean and square with the axis by machine, pipe cutter or saw as appropriate to materials, but not by flame cutting or bevel wheel cutter.

•	Pipes shall be prepared for capillary fittings on copper and stainless steel pipes by deburring and re-rounding.

•	Pipes shall be prepared for threading of steel pipes by removing burrs.

•	Pipes shall be prepared for butt welded steel pipelines by machining bevels and removing burrs.

•	Pipes shall be prepared on plastic pipelines in accordance with the manufacturer’s instructions, to suit solvent or heat fusion techniques for jointing.

2.4.	Screwed Threads

•	Screw threads shall be to BS 21 taper on pipes and adaptors. They shall be cut clean, concentric and unbroken with all oil, swarf, etc removed.

•	Shall be provided by means of capillary screwed adaptors on copper or stainless steel pipes with a limit of 2" BSP maximum.

•	Shall be painted on the exposed threads of mild steel pipes immediately the fitting has been screwed on.

2.5.	Pipe Unions, Flanges and Gaskets

•	Unions shall be limited to 2" BSP maximum size, or less if otherwise specified by the Engineer.

•	Flanges shall be provided on pipes 65mm diameter and above and on smaller pipes where specified in drawings, to suit particular requirements.

2.6.	Pipe Runs

•	Pipes shall be generally parallel with walls on horizontal runs and set neatly round piers and projections where a good appearance is required.

•	Pipes shall be arranged without joints where pipes pass through the thickness of walls, floors and structures.

•	Pipes shall be arranged with adequate clearance of walls and ceilings to allow easy access to valves.

2.7.	Open Ends of Pipework

•	Shall be temporarily sealed by the use of purpose made plugs, blanking caps, or blank flanges during pipework erection including valves at the end of pipework runs which shall be closed and sealed.

2.8.	Pipework Clearances

Minimum clearance between uninsulated pipes and adjacent surfaces shall be as follows: -

| Walls | 25mm |
| --- | --- |
| Ceilings | 100mm |
| Finished Floors | 150mm |
| Adjacent pipes | 25mm |
| adjacent to conduit or trunking | 150mm |

•	The spacing of services shall provide for:-

o	Increased spacing to accommodate pipeline fittings.

o	To pipes and electrical services for ease of installation, maintenance and inspection.

o	Layout and segregation of services to be in accordance with BS 8313.

o	Cold water pipes to be spaced from hot pipes to minimise heat gain.

2.9.	Sleeves

•	Sleeves shall be provided for pipes passing through walls, floors and partitions

•	Sleeves shall be generally one or two sizes larger than pipe as necessary and positioned true with pipe to provide adequate clearance and allow for lateral movements of pipeline if required.

•	Sleeves shall be finished flush with finished face of wall, floor and ceilings.

•	Sleeves shall be projected 75mm above floors in wet areas with the gap sealed with waterproof mastic.

•	Sleeves shall be supplied with lugs to locate in floors and ceilings.

•	Sleeves shall be fire-stopped in gap between pipe and sleeve in all fire rated structures.

•	Sleeves shall be oversize if insulation is to be carried through non-fire rated wall or partition as shown on the drawings.

2.10.	Air Venting

•	Air release valves shall be provided at all high points in water systems to facilitate complete removal of air.

•	valves shall be automatically operated unless specified.

2.11.	Pipe Supports

•	Shall be generally to the following standards.

o	BS 1494 Part 1, for pipe clips, brackets etc.

o	BS 3974, Part 1 for hangers, sliders and rollers.

o	BS 3974, Part 2 for clamps, cages, cantilevers and   beam attachments.

•	Shall be as detailed on the drawings and fastened only to the building structure at the specified positions.

•	Shall be arranged to support each pipe run independently of others, to permit differential expansion and maintenance without disturbing adjacent pipes.

•	Shall be installed so that pipes may expand and contract freely without overstressing pipes, joints or connections to equipment.

•	Shall be provided at base of vertical pipes, bends, tees, flanges, unions, and changes of direction, each side of valves, in conjunction with the normally spaced supports on horizontal and vertical runs.

•	Shall be fabricated from standard hot dipped galvanised mild steel rolled sections, or alternatively proprietary sections if specified in drawings, where built into walls or floors of ducts and subways.

2.12.	Spacing of Supports

TABLE OF MAXIMUM SPACINGS FOR PIPEWORK SUPPORTS

|  | Horizontal Spacings - Metres |  | Vertical Spacings - Metres |  |
| --- | --- | --- | --- | --- |
| Nominal Pipe Size mm | Steel or Iron Pipes | PVC or ABS Pipes | Steel or Iron Pipes | PVC or ABS Pipes |
| 15 | 1.8 | 0.8 |  | 1.2 |
| 20 | 2.4 | 0.8 | 3 | 1.2 |
| 25 | 2.4 | 0.9 | 3 | 1.3 |
| 32 | 2.4 | 1 | 3 | 1.5 |
| 40 | 2.4 | 1.1 | 3.7 | 1.6 |
| 50 | 2.4 | 1.1 | 3.7 | 1.6 |
| 65 | 3 | 1.1 | 4.6 | 1.6 |
| 80 | 3 | 1.1 | 4.6 | 1.6 |

2.13.	Electrolytic Action

•	Shall be prevented by ensuring that dissimilar metals are not in contact where the presence of water or moisture could promote electrolytic action.

•	Shall be prevented where copper pipes connect to ferrous cisterns or equipment, whether galvanised or not, by means of approved fibre washers or gaskets.

•	Shall be prevented by avoiding the need to join copper pipes to steel pipes.

•	Shall be prevented by using pipe supports as under: -

o	Galvanised malleable iron or steel for steel or iron pipes.

o	Brass or gunmetal for copper, stainless steel or plastic pipes.

2.14.	Compression Unions

•	Shall be generally comply with the performance requirements of BS 4368.

2.15.	Expansion Devices

•	Shall be fitted where expansion cannot be accommodated by natural offsets and changes of direction.

•	Shall in the case of expansion bellows, comply with BS 6129 Part 1.

•	Shall in the case of expansion loops, be manufactured from the same material as the pipe with additional thickness to allow for bending without undue thinning and formed in one length with ends flanged.

2.16.	Anchors

•	Shall be generally to BS 3974 Part 1 and BS 3974 Part 2  with steel brackets rigidly attached to the building structure or concrete blocks and/or as shown on the drawings.

•	Shall be suitable for test pressure loading.

•	Shall be positioned not nearer than 600mm to welded joints on steel pipes and secured so that the pipe is not deformed or overstressed by clamps, or where welded or brazed attachments are made, which shall be inspected and passed.

•	Shall be provided at stop ends, bends, junctions, valves and gradients steeper than 1 in 6. For buried mains of the non self-anchoring type.

•	Shall be provided on polyethylene buried mains as above and at mechanical joints where these are not designed to take end loads.

2.17.	Buried Pipework

•	Shall in the case of cold water pipes be HDPE, buried at a minimum depth of 600mm to top of pipe to suit local conditions and requirements of Central Water Authority.

•	Shall be laid on a bed of well rammed clean sand at least 100mm thick to underside and sides the trench sides to be clear of rocks or any other protruding debris.

•	Shall be finally backfilled with not less than 100mm thickness of the bedding material well rammed down on pipe before levelling off with soil free of rocks or other harmful debris. The work to be inspected before backfilling is commenced.

•	Shall be protected against possible damage by any future excavation work by the use of proprietary plastic warning marker tapes or 150mm wide mesh laid along the pipe run during backfilling and positioned between 150mm to 225mm below ground level, the tape or mesh to have a stainless steel wire for pipe detection on plastic systems.

•	Shall in the case of mains associated with fire fighting services, be governed also by any particular requirements of the Mauritius Fire and Rescue Service.

•	Where pipe is subjected to vehicular load, shall be protected by concrete surround with a minimum concrete cover of 300mm and concrete bedding of 100mm.

2.18.	Painting

•	Shall require all steel pipework and fittings to be supplied with manufacturer’s standard finish or protective coating.

•	Shall require all steel pipework other than galvanised to be thoroughly cleaned of all scale, corrosion, grease, etc, after erection and painted with corrosion resistant lead, copper, zinc, tin or aluminium free paint or coating suitable for service conditions.

2.19.	Testing of pipe and related accessories

2.19.1.	General

•	All individual parts forming the pipework circuit shall have been pressure tested by the manufacturers to British Standard or other recognised standards and certificates of soundness provided.

•	The installation shall then be pressure tested to prove soundness of joints and of the parts as installed.

2.19.2.	Flushing Out and Draining

•	Shall be undertaken before pressure tests are conducted and carried out using water.

•	Shall be witnessed to demonstrate that there are no blockages and that no foreign matter remains.

•	Shall be undertaken again when water is drained off after pressure testing to establish that the systems are still clean. On completion, all strainer cages shall be removed and cleaned and all dirt pockets opened up and cleaned.

•	Shall be arranged so that water systems are left dry after testing until setting-to-work and air systems left charged with reduced pressure air, monitored by a gauge to show any damage by other trades up to handover.

2.19.3.	Filling

•	Shall be carefully controlled in the case of hydraulically tested systems, to ensure that water hammer does not occur and demonstrated to show that all air has been vented off and the system is full and ready for testing.

•	Shall be similarly controlled when systems are re-filled for regulating, balancing, setting-to-work etc.

2.19.4.	Pressure Tests

•	Shall be to the pressures as detailed in the appropriate pipework service elements of this specification.

•	Shall be carried out in stages if advantageous and finally on the whole of each completed circuit or system.

•	Shall be undertaken before pipework is concealed by structures, covers, partitions, ceilings, insulation, backfilling over joints, final painting etc and when there is no danger of the water tested systems freezing.

•	Shall be carried out with all parts not designed to withstand the test pressure, removed or blanked off and the pipeline suitably anchored to withstand test pressure load.

•	Shall be witnessed and test certificates signed when the test is satisfactory.

2.20.	Service Identification

2.20.1.	General

	All services shall be identified in accordance with this specification.

	All services including valves and pipes shall be labelled and shall comply with BS 1710

2.20.2.	Colour Coding

	All services shall have the basic colour identifying the general contents (ie water, steam, gas etc). Colour coding shall comply with British Standard.

2.20.3.	Basic Colour

Shall be applied to the whole system or confined to basic colour bands at all valves, pipe, equipment and at intervals not greater than 3 metres throughout the pipework installation. Where basic colour bands are used, be placed on each side of the code colour. They shall have a minimum band width of 75mm for diameters up to 50mm and 150mm width for diameters above 50mm.

2.21.	Insulation for Hot water cPVC pipes

Insulating material shall be fire retardant, moisture resistant, flexible, closed cell, elastomeric nitrile rubber insulation of thermal conductivity 0.035 W/mK and minimum 65 kg/m3 material density similar or equivalent to Armacell (Class 'O' Armaflex).

3.	DRAINAGE SYSTEMS

3.1.	GENERAL

•	Sanitary pipework shall be installed in accordance with BS EN 12056-2.

•	Flexible pipe cannot be made concealed in blockwall. Any flexible connection shall be made such that they can be easily be replaced in the future.

•	Access caps shall be fitted at ends of all horizontal pipework, at junctions and changes of direction. Access caps shall be fitted at each floor level immediately above the highest connection, at the foot of each vertical stack and at junctions to horizontal connections to enable the system to be internally cleaned and rodded.  Access plates shall be provided on vertical stacks, at every level, above the rim of adjacent sanitary ware.

•	Cleaning eyes shall be provided on the end of horizontal waste floats and rodding eyes at the ends of horizontal soil manifolds, turned up to above the rim of adjacent WC pans.  Rodding eyes or access fittings shall be provided at changes of direction on suspended soil or waste pipework. Floor gullies shall be provided with drain access, either internally within the fitting or externally within the pipe run. Soil and waste branches shall be swept type.

•	At the penetration of all roof levels a suitable water seal and weathering shall be provided. Pipe stacks shall be carried up full bore above eaves or roof levels. Termination of soil, waste or ventilation pipework shall not be closer than 3 metres to any opening window, door or ventilation intake. Should this be unavoidable, the pipework shall be terminated 900mm above any such opening.

3.2.	PIPE AND FITTINGS

3.2.1.	Plastic Pipe and Fittings

•	Shall comprise UPVC pipe and fittings, manufactured by the injection moulding process. It shall for main soil, ventilation pipes and fittings be UPVC plastic to BS 4514.

•	Shall for all branch pipes, be provided with a radius swept in the direction of flow.

•	Shall not be fabricated by means of 'the cut and shut', hot air or solvent welded method.

3.3.	JOINTING OF PIPEWORK

3.3.1.	Plastics Pipe

•	Shall have UPVC plastic pipes and fittings, jointed by the solvent weld method.

•	Shall have spigot ends, squarely cut, ensuring continuity of the internal pipe bore.

•	Shall have excess jointing material removed and not allowed to accumulate on the internal surface of the pipe.

•	Shall accommodate thermal movement, by having joints formed using the joint ring system, with the spigot end of the pipe fitting in the direction of flow. All items forming the joint to be cleaned before assembly.

•	Shall be jointed using the correct solvent or lubricant and be installed to the Manufacturer's information.

3.4.	INSTALLATION OF PIPEWORK

3.4.1.	General

The installation of the above ground sanitation systems shall comply with the requirements of BS 5572 where applicable to design intent.

3.4.2.	Pipework Installation

Shall be installed to the minimum gradients specified in BS 5572 or as indicated on the drawing for all suspended runs.

- In general, the gradient for the pipe shall be as follows:

| - Type of waste | - Pipe size (mm) | - slope |
| --- | --- | --- |
| - Grey water | - All sizes | - 1:100 |
| - Black water | - 110 | - 1:55 |
|  | - 160 | - 1:80 |
|  | - 200 | - 1:90 |

3.4.3.	Pipe Clearances

Adequate separation from other engineering services and the structure shall be provided to enable maintenance to be carried out in an efficient manner with a minimum of disruption.

3.4.4.	Pipe Sleeves

•	Where passing through any part of the building fabric/blockwall, the pipes shall be accommodated in suitably sized sleeves of the same material as the pipe and be of such a diameter as to allow a minimum clearance for the free movement of the pipe.

•	The pipes shall where penetrating a fire resisting structure, shall be accommodated within a fire proof sleeve and which shall be filled with fire proof materials around to comply with Local Fire Services requirement and not less than that prescribed in the Building Regulations of the UK or any other equivalent standard.

•	Shall where passing through sleeves in external walls and ducts, be caulked between pipe and sleeve with lead wool or proprietary sealing compound.

•	Pipe sleeves shall not be used as a means of support to the pipes.

3.4.5.	Concealed pipe

No pipes shall be concealed within the building structure until satisfactory completion of the inspection and testing procedures.

3.4.6.	Buried pipe

All buried pipe shall have a minimum cover of 600 mm or as specified elsewhere by the engineer.

Where pipe is subjected to vehicular load, shall be protected by concrete surround with a minimum concrete cover of 300mm and concrete bedding of 100mm.

3.4.7.	Manhole/Gully trap/Inspection chamber

Provision of manholes

In general, manholes or inspection chambers should be provided in the following situations:

•	At all changes of direction on drains.

•	At all changes of gradient on drains.

•	At all drain junctions.

•	At the head of each length of drain.

•	At all changes in pipe diameter

All manholes/Gully traps/Inspection chamber shall have a minimum depth of 600mm, except as specified elsewhere.

Appropriate benching shall be provided to prevent the splashing of waste and water from incoming branch lines as this causes waste to build up in the manhole leading to blockages.

Splashing of waste into manhole shall not be allowed. All incoming waste into a manhole shall be made via appropriate benching.

Note: Elbow and Y-piece connection to buried pipe shall not be accepted.

3.4.8.	Traps

•	Shall conform to BS 5572 and all relevant British Standards. They shall be to BS 3943 or the equivalent French Standard. They shall generally be 'P' traps unless otherwise specified in drawings.

•	Shall for all sanitary fittings and equipment be a two piece tubular trap, where exposed under basins be chromium plated copper alloy bottle traps.

3.4.9.	Sanitary Appliance Connections

Shall be by a dry seal push fit joint to the drainage system for all connections from sanitary appliance outlets 89mm diameter and above.

3.4.10.	Access Points – GENERAL

•	Shall be provided into the pipe bore to enable testing, inspection and efficient maintenance operations to be carried out. They shall be all fully accessible.

•	They shall have all access plates and caps fitted as the installation work proceeds and remain sealed except for inspection and testing. In the event of an open access point being found at any time during the course of installation, the contractor shall have that section of pipework rodded out and flushed with clean water. Should it be demonstrated that the pipe bore is not satisfactorily finished, the section adjacent to the access point to be stripped out to a location of satisfactory internal finish.

•	Access points on vertical main soil and ventilation pipes of 76mm -160mm diameter, shall be provided in the following positions: -

o	Above the spill-over level of adjacent sanitary fittings and a minimum of one metre above finished floor level on all floors.

o	Above offsets in vertical stacks.

o	At all junctions in suspended runs and in other positions as indicated on the drawings.

o	Access points shall not be located at high level in clinical areas.

o	At all change in direction

3.4.11.	UPVC/Polypropylene Pipe Access Points

•	Shall be full width and bolted, integral with a purpose made fitting, or cut and located in positions shown on the drawings where located on the side of UPVC and Polypropylene pipes.

•	Shall be solvent welded plugs with screwed caps, where located on the end of UPVC pipes and fixed by compression screwed caps on polypropylene pipes.

3.4.12.	Sanitary Appliances

•	All sanitary appliances shall be fixed in accordance with BS 8000: Part 13. They shall have all outlets and overflows bedded into the sanitary appliances together with all washers, wedges and other sundries necessary to complete an efficient fixing.

•	All debris shall be removed and the appliance cleaned and protected from damage and abuse on completion of fixing.

•	Sanitary appliances shall be tested by operation of taps to ensure overflow waterways are clear of mastic sealant.

•	Shall be subjected to discharge tests to determine the integrity of trap seal under normal operating conditions as defined in BS 5572: Performance Tests.

3.5.	SUPPORTS EXPANSION AND ANCHORS

3.5.1.	Pipe Supports

•	Shall be provided in accordance with the requirements of BS 5572. They shall be provided with supports located at intervals not greater than the following Table for suspended and vertical pipes:-

| Support distance for vertical and suspended pipes |  |  |  |
| --- | --- | --- | --- |
| PIPE MATERIAL | NOMINAL BORE (mm) | VERTI VERTICAL RUN (m) | HORIZONTAL RUN(M) |
| UPVC | 32-40 | 1.2 | 0.5 |
|  | 50 | 1.2 | 0.6 |
|  | 75 – 100 | 1.8 | 0.9 |
|  | 150 | 1.8 | 1.2 |
| *Polypropylene Mechanical Joints | 38 |  | 0.5 |
|  | 51 | 1.2 | 0.5 |
|  | 76 |  | 1.5 |
|  | 102 |  | 1.8 |

•Suspended pipe shall be continuously supported where temperatures in excess of 20°C are maintained. They shall be fixed to the structure at two points and have vertical adjustment facilities for suspended pipes.

•	Anchors and supports be provided on suspended and vertical UPVC pipes between fixed points to maintain stability under temperature change.

3.6.	CARE OF PIPES

3.6.1.	Sealing Open Ends of Pipes

Sealing of pipes shall be carried out as the installation proceeds. It shall comprise purpose-made metal or plastic plugs, caps or blank flanges. In the event of an open ended pipe being found or a plug removed, the Contractor shall have the section concerned rodded clean and flushed with clean water. If after such clearing operations it can be demonstrated that the pipe bore has not been satisfactorily cleaned, the pipes adjacent to the open end to be stripped out to a location of clean internal finish.

3.6.2.	Pipe Condition and Protection

All pipes to be used shall be straight, cleanly finished, round in cross section and without defect.

3.6.3.	Pipe Cutting

•	Shall include for all pipes to be cut clean and square with axis of the pipe and before installation, the cut ends of the pipe to be made smooth and any burrs removed by filing.

4.	INSPECTION, TESTING AND COMMISSIONING

4.1.	GENERAL

•	The entire Works shall be inspected, tested and commissioned in accordance with all relevant British Standard Specifications and Codes of Practice together with and the details given in this Specification to the entire satisfaction of the Engineer.

•	No section of the Works shall be insulated or in any other way concealed prior to testing and inspection.

•	Open and closed circuit systems shall be flushed through to remove scale and debris collected within the systems. On completion of flushing they shall with the exception of domestic water systems be chemically as necessary.

•	The engineer shall be advised at least five working days before in advance of the commencement of the flushing and cleaning programme so that procedures can be witnessed.

4.2.	ATTENDANCE

•	Tests shall be arranged in co-operation with the Mechanical Services Installer and Engineer who shall be given five working days notice in writing of the time, location and nature of the test to be performed. No test shall be considered valid unless the Engineer or his appointed representative is present.

4.3.	COMMISSIONING/TEST EQUIPMENT

•	All necessary facilities, measuring and recording instruments including test pumps and gauges for inspection or testing purposes shall be provided and shall be checked or calibrated by the Mechanical Services Installer or Mauritius Standard Bureau as necessary before use. The Engineer reserves the right to call for a demonstration of the accuracy of any instruments provided.

4.4.	DRAINAGE SYSTEM

4.4.1.	Ball test

•	After completion of the work the contractor shall be required to undertake a ball test for freedom from obstruction, gradient and for circularity inside the pipe.

•	A ball (less than the diameter of the drain pipe) shall be rolled through the drain

4.5.	WATER SUPPLY SYSTEM

4.5.1.	FILLING

•	The system shall be filled.

•	All dirt pockets and strainers shall be inspected and cleaned out. The system shall then be refilled with the dirt pockets and strainers checked each time

4.5.2.	FLUSHING

•	Flushing of closed water systems shall be carried out strictly in accordance with BSRIA application Guides AG1/2001 and AG2/89.3. Flushing shall commence within 24 hours of the filling described above being completed.

4.5.3.	PRESSURE TEST

•	The system shall be pressure tested as specified elsewhere.

4.6.	FAILURE OF TEST

•	Any defects occurring at any time during the test duration shall be made good and a complete re-test carried out.

•	Where failure during a test, inspection or commissioning process results in damage to the building fabric to any services not provided as part of this Contract, or requires subsequent builders work in connection to be carried out, then the remedial works shall be the responsibility of the Mechanical Services Installer.

•	Leakages shall be repaired by properly remaking or replacing the defective component. Caulking will not be permitted

4.7.	TEST/COMMISSIONING RESULTS

•	Prior to undertaking of the commissioning exercise the contractor shall be required to undertake test and send results to the Engineer. Should the result be satisfactory, the Engineer shall be present to witness the commissioning exercise.

•	On completion of each section of work the results shall be typed in schedule form and submitted to the Engineer for comment. Following comment by the Engineer the tabulated commissioning results shall be incorporated into the Operation & maintenance manuals.

4.8.	WARRANTY

•	A minimum of I year warranty shall be provided on all equipment, except as specified elsewhere.

5.	DRAWINGS AND DOCUMENTATION

5.1.	TENDER DRAWINGS

•	The Tender Drawings are prepared by the Engineer to show the general arrangement of the plant, equipment and services, which form the intended Contract. The drawings are prepared in sufficient detail to, in conjunction with the Specification, allow competitive Tenders to be submitted.

•	The Tender drawings show the design intent.

•	The Mechanical Services Installer shall be responsible for interpreting the drawings, making due allowance for offsets to avoid the building structure or other services, whether indicated or not. The Mechanical Services Installer shall take all necessary steps to fully acquaint him with the nature and extent of the works by visiting the site and inspecting the architectural, structural and other services drawings.

•	No claim for loss or expense due to the above factors will be considered.

5.2.	SHOP DRAWINGS

•	The Contractor Installer shall produce fully detailed and dimensioned shop drawings of each service to be installed, including all purpose made plant and equipment. The location of all plant, equipment and services shall be fully dimensioned from each other, from other work and from the building structure. Exact dimension of approved equipment shall be shown in the drawing.

•	Shop drawings shall be issued prior to start of any Mechanical Work.

•	The Mechanical Services Installer shall ensure that all services, including those provided by others are fully co-ordinated with each other and with the building structure and finishes.

•	The services shall be presented in different sheets as shown in the Tender drawings. Merging of different services in the same sheet shall not be accepted.

•	Shop drawings shall include fully dimensioned details and positions of supports and fixings.

•	Working drawings shall be produced in accordance with a programme which is to be agreed with the Contractor to suit the overall programme for the Works.  Reasonable allowance shall be made for incorporating any comments made by the Engineer.

•	Dimensions shall be clearly shown to locate plant, equipment and distribution from the building structure or fabric and from each other. Inverts or levels above datum shall be shown for all distribution services.

•	Drawings shall be produced in A1 size paper with scale not more than the that used in tender drawing.

•	The drawings shall also include all builders work associated with the mechanical drawings.

•	 All drawing shall be signed by a Registered Mechanical Engineer.

5.3.	ISSUE OF DRAWINGS

•	Three prints of the drawings shall be issued to the Engineer for this purpose. A period of minimum fifteen working days shall then be allowed for comment on the drawings by the Engineer. All shop drawings shall be accompanied by a covering letter.

•	When the drawings have been amended to incorporate any changes, three copies shall be issued to the Architect and the Engineer.

5.4.	DIMENSIONS

•	The Mechanical Services Installer shall take site dimensions during the preparation of the drawings and be responsible for their accuracy. Setting out of the works on site shall be carried out by the Mechanical Services.

•	Installer and any errors arising from inaccuracies in setting out shall be the Mechanical Services Installers responsibility.

•	The Mechanical Services Installer shall be solely responsible for the accuracy of the drawings and for any equipment shown being suitable for the purpose for which it is intended and in accordance with the design drawings and specifications.

5.5.	SITE COPIES

•	One set of prints of working drawings, manufacturing drawings and installation drawings as necessary to provide a complete record of the Works shall be kept on site. The drawings shall be available at all times for inspection by the Engineer.

5.6.	MANUALS

•	Three sets of manuals shall be submitted to the Engineer for comments prior to onward submission to the Employer.

•	The manual shall be in A4 size and shall include the following: -

Section 1	Description of the system installed/content of the Manual

Section 2	Description of how to operate and shut down the system or main equipment of the system.

Section 3 	Procedures for undertaking the planned preventive maintenance. Maintenance frequency for each part to be highlighted.

Section 4 	List of equipment that have been installed.

Section 5	As made Drawings

Section 6	Emergency Measures. This shall include telephone numbers of Mechanical Services Installer's emergency staff and name, address

Section 7	Copies of all test certificates and commissioning data for each service and item of plant and equipment.

5.7.	ASMADE DRAWINGS

As Made Drawings shall show the work as completed and shall record the following as far as possible: -

o	The location of Services including size and materials of pipes and other relevant information.

o	The layout, location and extent of all piped services showing pipe sizes, together with all valves and other instruments.

o	Detailed general arrangements of plant room.

o	Sections, elevations and schematics of the plant spaces required to clearly indicate the plant arrangements.

o	The As made Drawings shall be drawn using the current version of Autocad. Lettering height shall be not less than 2.5mm times the scale of drawing.

5.8.	MATERIAL APPROVAL

•	Prior to installation of any material in site, the contractor shall seek approval of these materials from the Engineer. The request shall be submitted along with a covering letter and technical documentation including catalogues. The contractor shall be required to highlight each proposed material in the catalogue.

•	Any deviation from the Engineer’s specification shall be highlighted in the contractor’s submission.

5.9.	SAMPLES

•	As part of the material approval process, the contractor shall be required to send sample of proposed materials including pipes, valves, fittings complete with all related accessories.

•	All sample shall be displayed on a sample board on site.

EQUIPMENT SCHEDULE

- Valves Schedule

Note: All valves shall be of European Origin

| Valves Type | Location | Material |
| --- | --- | --- |
| Cold water system |  |  |
| Isolating valve | Throughout | Bronze or brass body, stainless steel lever |
| Angle valve | Water closets | Chromium plated |
| Non-return valve | Throughout | Bronze or brass body |
| Automatic air vent (air release valve) | End of pipe | Brass |

- Floor trap schedule

| REFERENCE | FLOOR TRAP |
| --- | --- |
| Location | Toilets |
| Discharge dia | 40 mm OD |
| Trap material | PVC |
| Cover material | Stainless Steel |
| Cover fixation | Vandal proof screws (Allen Key) |
| Spigot outlet | Horizontal |
| Size | 100 mm x 100 mm |
| Water seal | Minimum 50mm |

- Firefighting equipment Schedule

| Description | Fire extinguisher |
| --- | --- |
| Location | Throughout the building |
| Type | ABC |
| Capacity | 4 kg |
| Paint Finish | Red |
| Fire Rating | 13A 70B |
| Type of Fire | A,B,C,E |
| Mode of operation | Manual |
| Compliance | British/European Standard or MS 1539 |

| Description | Fire extinguishers |
| --- | --- |
| Location | Throughout the building |
| Type of Extinguishant | Carbon dioxide |
| Capacity | 2 Kg |
| Paint Finish | Red |
| Fire Rating | 21B |
| Mode of operation | Manual |
| Compliance | British/European Standard or MS 1539 |

- Schedule for signage

| Ref | Description | Min Size (mm) | Geometric shape | Safety colour | Contrast colour | Graphical symbol colour |
| --- | --- | --- | --- | --- | --- | --- |
| Type B | Fire extinguisher identification signs incorporating graphical symbols indicating ‘ CO2’ | 200x80 | Rectangular | Red | White | White |
| Type C | Fire extinguisher identification signs incorporating graphical symbols indicating ‘ABC’ | 200x80 | Rectangular | Red | White | White |
| Material | Photoluminescent rigid PVC fire signs on Perspex background screwed to background concrete. |  |  |  |  |  |
| Flammability | Fire retardant. |  |  |  |  |  |

- Pipe schedule

| SERVICE | LOCATION | PIPEWORK MATERIAL | PRESSURE RATING | PROTECTION |
| --- | --- | --- | --- | --- |
| Cold Water Pipes | In Riser duct | uPVC | PN16 | No |
|  | In Boxing | uPVC | PN16 | No |
|  | On Roof/facade | uPVC | PN16 | 2 layers of UV protection paint. |
|  | Underground (On Site) | HDPE | PN16 | Concrete surround where cross roads. |
| Soil, waste and vent pipes | In Riser duct | PVC | PN 6 | No |
|  | Underground | PVC | SN8 | No |
|  | Cast in Slab/floor | PVC | PN16 for pipes | No |

- Tank

| Description | Water tank for potable water supply |
| --- | --- |
| Material | Fibre glass/polyethylene |
| Location | Site and roof |
| Capacities (Lts) | 9000/2000 |
| Installation requirements | Installed and securely fixed on concrete platform and free from debris. |
| Fixation | Tank to be secured by lifting/holding lugs. Fixation to ensure tank to withstand cyclonic condition when empty. |
| Accessories | -Manhole and removable cover -Air Vent -min 25mm Float valve at inlet, with external BSP thread -Holding/ Lifting lugs -provision for cable for float switch - Outlet of tank shall be of the same size as the pipe shown in drawings. |

- Pump

| Description | Domestic Pump Set. |
| --- | --- |
| Location | Pump room (on site) |
| System | Cold Water System |
| No of Pumps | 2 vertical/horozontal centrifugal pumps on common base plate and manifold. |
| Control Sequence of Pumps | Duty/ assist/Standby (auto-changeover) Notes: - Each pump shall operate in duty mode alternately such that the wear and tear for each pump is the same. - Should the water demand increase further then the assist pump shall switch on automatically and both pump to work in parallel. - In case the duty pump is failed, the standby/assist pump to start automatically. |
| Flow rate per Pump | 1.0 l/s |
| Head per pump | 35 m |
| Valves | As per schematic diagram |
| Shaft/Impeller | Stainless steel |
| Operating efficiency | Contractor to specify |
| Method of control | Pressure Switches |
| Max electrical Rating per pump per Set (kW) | 2.5 |
| Power Supply (ph/V/Hz) | Single phase |
| Drive | variable speed drives fitted with pumps |
| Pressure vessel | 1 x 25L |
| NOTES | To be provided as a complete package unit with all interconn1.1ecting pipework and wiring, suitable for floor mounting. Low water level cut-out by control impulse, pressure switch, adjustable stop-time delay on low water. |

A.	DRAWINGS

  - LIST OF DRAWINGS.

  - Drawings:  A. Architectural -20 sheets

B. structural -23 sheets

C. Electrical – 6 Sheets

D. Mechanical – 8 sheets

E. Site Works -7 Sheets

Note: Drawings will be forwarded by email to bidders on application (PDF file). Prospective bidders may please submit their email address to:-

The General Manager

THE SILWF -15-21 Edith Cavell St. Port Louis

Email Address: - silwf@intnet.mu

Phone No:- 2113530

Community Wellness Centre at Gokhoola 

List of Architectural Drawings

|  | DRG NO. | TITLE |
| --- | --- | --- |
| 01 | G859-SW-01 | Site Plan (Survey) |
| 02 | G859-SW-02 | Demolition Plan |
| 03 | G859-SW-03 | Site Plan |
| 04 | G859-01 | Ground Floor Plan |
| 05 | G859-02 | Lower Roof Plan |
| 06 | G859-03 | Upper Roof Plan |
| 07 | G859-04 | Sections / Toilet for Disabled Details |
| 08 | G859-05 | Sections Gargole Details |
| 09 | G859-06 | Elevations (Front and RHS) |
| 10 | G859-07 | Elevations (Rear and LHS) |
| 11 | G859-08 | Schedules of Openings Sheet 1 |
| 12 | G859-09 | Schedules of Openings Sheet 2 |
| 13 | G859-10 | Schedules of Finishes, Sanitary Wares & Burglar Proofing |
| 14 | G859-11 | Details |
| 15 | G859-12 | Details (Garbage Bins, Boundary Wall, Pump House, Conc. Platform) |
| 16 | G859-13 | Details (Signace) |
| 17 | G859-14 | Details (Skylight, Emergency Fire Exit Door, CEB Cubicle) |
| 18 | G859-15 | Details (Signboard and Temporary Hoarding) |
| 19 | G859-16 | Details (False Ceiling) |
| 20 | G859-17 | Details (Catchpit, Soakaway, Flag Pole) |

Community Wellness Centre at Gokhoola

List of Structural Drawings

|  | DRG NO. | TITLE |
| --- | --- | --- |
| 01 | G859/ST-01 | Foundation layout |
| 02 | G859/ST-02 | Foundation details Sht 1 |
| 03 | G859/ST-03 | Foundation details Sht 2 |
| 04 | G859/ST-04 | RC details of columns |
| 05 | G859/ST-05 | Ground floor layout & sections |
| 06 | G859/ST-06 | Sections to Ground Floor layout Sht 1 |
| 07 | G859/ST-07 | Sections to Ground Floor layout Sht 2 |
| 08 | G859/ST-08 | Sections to Ground Floor layout Sht 3 |
| 09 | G859/ST-09 | Sections to Ground Floor layout Sht 4 |
| 10 | G859/ST-10 | RC details of Ground beams |
| 11 | ED859/ST-11 | Roof layout & Sections |
| 12 | G859/ST-12 | RC details of Roof beams Sht 1 |
| 13 | G859/ST-13 | RC details of Roof beams Sht 2 |
| 14 | G859/ST-14 | RC details of Roof beams Sht 3 |
| 15 | G859/ST-15 | RC details of Roof beams Sht 4 |
| 16 | G859/ST-16 | RC details of Roof beams Sht 5 |
| 17 | G859/ST-17 | RC details of Roof beams Sht 6 |
| 18 | G859/ST-18 | RC details of Roof Slab |
| 19 | G859/ST-19 | Layout & RC details of staircase |
| 20 | G859/ST-20 | Staircase Roof layout & details |
| 21 | G859/ST-21 | Details of Pergola |
| 22 | G859/ST-22 | Standard Structural details |
| 23 | G859/ST-23 | General Structural Notes |

Community Wellness Centre at Gokhoola 

List of Electrical Drawings

| DRG NO. | TITLE |
| --- | --- |
| G859-EL-01 | Site Plan Electrical Works |
| G859-EL-02 | Electrical Works – Lighting |
| G859-EL-03 | Electrical Works – Socket and AC Layout |
| G859-EL-04 | Electrical Works – Fire Alarm |
| G859-EL-05 | Electrical Works – MDB Schematics and Layouts |
| G859-EL-06 | Electrical Works – Schematics |

Community Wellness Centre at Gokhoola 

List of Mechanical Drawings

| DRG NO. | TITLE |
| --- | --- |
| G859/LS01 | List of drawings |
| G859/ME/DR/-01 | Site Plan Drainage System |
| G859/ME/DR-02 | Ground Floor Plan Drainage System |
| G859/ME/DR-03 | Details Drainage System |
| G859/ME/CW-01 | Site Plan – Cold water distribution System |
| G859/ME/CW-02 | Ground Floor Cold Water Distribution System |
| G859/ME/CW-03 | Roof Cold Water Distribution System |
| G859/ME/CW-04 | Schematic layout – Cold Water distribution System |

Community Wellness Centre at Gokhoola 

List of Site Works drawings

| DRG NO. | TITLE |
| --- | --- |
| G859/SW/ST01 | Site works layout |
| G859/SW/ST02 | R.C details of boundary wall Type I Retraining Wall Type I, II Sections and hoarding |
| G859/SW/ST03 | Details of Platform for water reticulation. Tank, Green Pavers, Kerb, Manholes, Gully trap and Soakaway |
| G859/SW/ST04 | Structural details of Pump House |
| G859/SW/ST05 | Structural details of Garbage Bin |
| G859/SW/ST06 | R.C details of Septic Tank |
| G859/SW/ST07 | Structural details of CEB Cubicle |

Section IV:  General Conditions of Contract and Particular Conditions of Contract

Any resulting contract shall be placed by means of a Letter of Acceptance and shall be subject to the General Conditions of Contract (GCC), 
(Ref: W/GCC10/12-21), for the Procurement of Works (available on website ppo.govmu.org) except where modified by the Particular Conditions of Contract below.

Procurement Reference Number:	______________________________

Procurement Policy Office

(Established under section 4 of the Public Procurement Act 2006)

Ref: W/GCC10/12-21

GENERAL CONDITIONS OF CONTRACT

(WORKS)

Procurement Policy Office

Ministry of Finance and Economic Development

Port Louis

December 2021

AMENDMENTS TO DOCUMENT DATED 16 DECEMBER 2021

Section VI: General Conditions of Contract

Sub-clause 55.2 & 59.3 (Added)

Sub-clause 57.4 (Amended)

AMENDMENTS TO DOCUMENT DATED 15 OCTOBER 2020

Section VI: General Conditions of Contract

Sub-clause 18.3 (Amended)

AMENDMENTS TO DOCUMENT DATED 17 April 2020

Section VI: General Conditions of Contract

Sub-clause 7.1 (Amended)

AMENDMENTS TO DOCUMENT DATED 08 April 2020

Section VI: General Conditions of Contract

Sub-clause 3.2 (Added)

Sub-clause 18.1 (Amended)

Sub-clause 18.2 & 18.3 (Added)

Sub-clause 39.2 & 39.6 (Amended)

Sub-clause 40.1 (Amended)

Sub-clause 40.5 (Added)

Sub-clause 49.1 (Amended)

Sub-clause 53.2 (Added)

AMENDMENTS TO DOCUMENT DATED 21 MAY 2018

Section VI: General Conditions of Contract

Sub-clause 39.1 & 39.2 (Amended)

Sub-clause 40.1 (Amended)

AMENDMENTS TO DOCUMENT DATED 20 MARCH 2018

Section VI: General Conditions of Contract

Sub-clause 46.1 (Amended)

AMENDMENTS TO DOCUMENT DATED 06 MAY 2014

Section VI: General Conditions of Contract

Sub-clause 49.2 (c) (Amended)

AMENDMENTS TO DOCUMENT DATED 17 OCTOBER 2013

Section VI: General Conditions of Contract

Clause 58 (Amended)

(Public Body)

- General Conditions of Contract

- Table of Clauses

- A.  General	165

- 1.	Definitions	165

- 2.	Interpretation	167

- 3.	Language and Law	Error! Bookmark not defined.

- 4.	Project Manager’s Decisions	168

- 5.	Delegation	168

- 6.	Communications	168

- 7.	Subcontracting	168

- 8.	Other Contractors	168

- 9.	Personnel and Equipment	169

- 10.	Employer’s and Contractor’s Risks	169

- 11.	Employer’s Risks	169

- 12.	Contractor’s Risks	169

- 13.	Insurance	170

- 14.	Site Data	170

- 15.	Contractor to Construct the Works	170

- 16.	The Works to Be Completed by the Intended Completion Date	170

- 17.	Approval by the Project Manager	171

- 18.	Safety……….	171

- 19.	Discoveries	171

- 20.	Possession of the Site	171

- 21.	Access to the Site	171

- 22.	Instructions	172

- 23.	Appointment of the Adjudicator	172

- 24.	Procedure for Disputes	172

- B.  Time Control	173

- 25.	Program	173

- 26.	Extension of the Intended Completion Date	174

- 27.	Acceleration	174

- 28.	Delays Ordered by the Project Manager	174

- 29.	Management Meetings	174

- 30.	Early Warning	175

- C.  Quality Control	175

- 31.	Identifying Defects	175

- 32.	Tests………….	175

- 33.	Correction of Defects	175

- 34.	Uncorrected Defects	175

- D.  Cost Control	175

- 35.	Contract Price	175

- 36.	Changes in the Contract Price	176

- 37.	Variations	176

- 38.	Cash Flow Forecasts	177

- 39.	Payment Certificates	177

- 40.	Payments	178

- 41.	Compensation Events	179

- 42.	Tax		180

- 43.	Currencies	180

- 44.	Price Adjustment	180

- 45.	Retention	181

- 46.	Liquidated Damages	181

- 47.	Bonus	181

- 48.	Advance Payment	182

- 49.	Securities	182

- 50.	Dayworks	184

- 51.	Cost of Repairs	184

- 52.	Labour Clause	184

- E.  Finishing the Contract	185

- 53.	Completion	185

- 54.	Taking Over	185

- 55.	Final Account	185

- 56.	Operating and Maintenance Manuals	185

- 57.	Termination	186

- 58.	Fraud / Corruption and Integrity Clause	186

- 59.	Payment upon Termination	187

- 60.	Property	188

- 61.	Release from Performance	188

General Conditions of Contract

A.  General

| - Definitions | - Boldface type is used to identify defined terms. - The Accepted Contract Amount means the amount accepted in the Letter of Acceptance for the execution and completion of the Works and the remedying of any defects. - The Activity Schedule is a schedule of the activities comprising the construction, installation, testing, and commissioning of the Works in a lump sum contract. It includes a lump sum price for each activity. - The Adjudicator is the person appointed jointly by the Employer and the Contractor to resolve disputes in the first instance, as provided for in GCC 23. - Bill of Quantities means the priced and completed Bill of Quantities forming part of the Bid. - Compensation Events are those defined in GCC Clause 41 hereunder. - The Completion Date is the date of completion of the Works as certified by the Project Manager, in accordance with GCC Sub-Clause 53.1. - The Contract is the Contract between the Employer and the Contractor to execute, complete, and maintain the Works. It consists of the documents listed in GCC Sub-Clause 2.3 below. - The Contractor is the party whose Bid to carry out the Works has been accepted by the Employer. - The Contractor’s Bid is the completed bidding document submitted by the Contractor to the Employer. - The Contract Price is the Accepted Contract Amount stated in the Letter of Acceptance and thereafter as adjusted in accordance with the Contract. - Days are calendar days; months are calendar months. - Dayworks are varied work inputs subject to payment on a time basis for the Contractor’s employees and Equipment, in addition to payments for associated Materials and Plant. - A Defect is any part of the Works not completed in accordance with the Contract. - The Defects Liability Certificate is the certificate issued by Project Manager upon correction of defects by the Contractor. - The Defects Liability Period is the period named in the PCC pursuant to Sub-Clause 33.1 and calculated from the Completion Date. - Adjudicator means the single person appointed under Clause 23. - Drawings means the drawings of the Works, as included in the Contract, and any additional and modified drawings issued by (or on behalf of) the Employer in accordance with the Contract, include calculations and other information provided or approved by the Project Manager for the execution of the Contract. - The Employer is the party who employs the Contractor to carry out the Works, as specified in the PCC. - Equipment is the Contractor’s machinery and vehicles brought temporarily to the Site to construct the Works. - “In writing” or “written” means hand-written, type-written, printed or electronically made, and resulting in a permanent record; - The Initial Contract Price is the Contract Price listed in the Employer’s Letter of Acceptance. - The Intended Completion Date is the date on which it is intended that the Contractor shall complete the Works. The Intended Completion Date is specified in the PCC. The Intended Completion Date may be revised only by the Project Manager by issuing an extension of time or an acceleration order. - Materials are all supplies, including consumables, used by the Contractor for incorporation in the Works. - Plant is any integral part of the Works that shall have a mechanical, electrical, chemical, or biological function. - The Project Manager is the person named in the PCC (or any other competent person appointed by the Employer and notified to the Contractor, to act in replacement of the Project Manager) who is responsible for supervising the execution of the Works and administering the Contract. - PCC means Particular Conditions of Contract - The Site is the area defined as such in the PCC. - Site Investigation Reports are those that were included in the bidding documents and are factual and interpretative reports about the surface and subsurface conditions at the Site. - Specification means the Specification of the Works included in the Contract and any modification or addition made or approved by the Project Manager. - The Start Date is given in the PCC. It is the latest date when the Contractor shall commence execution of the Works. It does not necessarily coincide with any of the Site Possession Dates. - A Subcontractor is a person or corporate body who has a Contract with the Contractor to carry out a part of the work in the Contract, which includes work on the Site. - Temporary Works are works designed, constructed, installed, and removed by the Contractor that are needed for construction or installation of the Works. - A Variation is an instruction given by the Project Manager which varies the Works. - The Works are what the Contract requires the Contractor to construct, install, and turn over to the Employer, as defined in the PCC. |
| --- | --- |
| - Interpretation | - In interpreting these GCC, words indicating one gender include all genders. Words indicating the singular also include the plural and words indicating the plural also include the singular. Headings have no significance. Words have their normal meaning under the language of the Contract unless specifically defined. The Project Manager shall provide instructions clarifying queries about these GCC. - If sectional completion is specified in the PCC, references in the GCC to the Works, the Completion Date, and the Intended Completion Date apply to any Section of the Works (other than references to the Completion Date and Intended Completion Date for the whole of the Works). - The documents forming the Contract shall be interpreted in the following order of priority: - The Agreement, - Letter of Acceptance, - Contractor’s Bid, - Particular Conditions of Contract, - General Conditions of Contract, - Specifications, - Drawings, - Bill of Quantities, and - any other document listed in the PCC as forming part of the Contract. |
| - Contract Agreement | - The language of the Contract and the law governing the Contract are stated in the PCC. - The parties shall enter into a Contract Agreement within 28 days after the contractor receives the Letter of Acceptance unless they agree otherwise. |
| - Project Manager’s Decisions | - Except where otherwise specifically stated, the Project Manager shall decide contractual matters between the Employer and the Contractor in the role representing the Employer. |
| - Delegation | - Otherwise specified in the PCC, the Project Manager may delegate any of his duties and responsibilities to other people, except to the Adjudicator, after notifying the Contractor, and may revoke any delegation after notifying the Contractor. |
| - Communications | - Communications between parties that are referred to in the Conditions shall be effective only when in writing. A notice shall be effective only when it is delivered. |
| - Subcontracting | - The Contractor may subcontract with the approval of the Project Manager, but may not assign the Contract without the approval of the Employer in writing. Subcontracting shall not alter the Contractor’s obligations and the contractor shall be liable for the non-performance or improper performance of the obligations of the subcontractor. |
| - Other Contractors | - The Contractor shall cooperate and share the Site with other contractors, public authorities, utilities, and the Employer between the dates given in the Schedule of Other Contractors, as referred to in the PCC. The Contractor shall also provide facilities and services for them as described in the Schedule. The Employer may modify the Schedule of Other Contractors, and shall notify the Contractor of any such modification. |
| - Personnel and Equipment | - The Contractor shall employ the key personnel and use the equipment identified in its Bid, to carry out the Works or other personnel and equipment approved by the Project Manager. The Project Manager shall approve any proposed replacement of key personnel and equipment only if their relevant qualifications or characteristics are substantially equal to or better than those proposed in the Bid. - If the Project Manager asks the Contractor to remove a person who is a member of the Contractor’s staff or work force, stating the reasons, the Contractor shall ensure that the person leaves the Site within seven days and has no further connection with the work in the Contract. |
| - Employer’s and Contractor’s Risks | - The Employer carries the risks which this Contract states are Employer’s risks, and the Contractor carries the risks which this Contract states are Contractor’s risks. |
| - Employer’s Risks | - From the Start Date until the Defects Liability Certificate has been issued, the following are Employer’s risks: - The risk of personal injury, death, or loss of or damage to property (excluding the Works, Plant, Materials, and Equipment), which are due to - use or occupation of the Site by the Works or for the purpose of the Works, which is the unavoidable result of the Works or - negligence, breach of statutory duty, or interference with any legal right by the Employer or by any person employed by or contracted to him except the Contractor. - The risk of damage to the Works, Plant, Materials, and Equipment to the extent that it is due to a fault of the Employer or in the Employer’s design, or due to war or radioactive contamination directly affecting the country where the Works are to be executed. - From the Completion Date until the Defects Liability Certificate has been issued, the risk of loss of or damage to the Works, Plant, and Materials is an Employer’s risk except loss or damage due to - a Defect which existed on the Completion Date, - an event occurring before the Completion Date, which was not itself an Employer’s risk, or - the activities of the Contractor on the Site after the Completion Date. |
| - Contractor’s Risks | 12.1 From the Starting Date until the Defects Liability Certificate has been issued, the risks of personal injury, death, and loss of or damage to property (including, without limitation, the Works, Plant, Materials, and Equipment) which are not Employer’s risks are Contractor’s risks. |
| - Insurance | - The Contractor shall provide, in the joint names of the Employer and the Contractor, insurance cover from the Start Date to the end of the Defects Liability Period, in the amounts and deductibles stated in the PCC for the following events which are due to the Contractor’s risks: - loss of or damage to the Works, Plant, and Materials; - loss of or damage to Equipment; - loss of or damage to property (except the Works, Plant, Materials, and Equipment) in connection with the Contract; and - personal injury or death. - Policies and certificates for insurance shall be delivered by the Contractor to the Project Manager for the Project Manager’s approval within 21 days after issue of letter of Acceptance. All such insurance shall provide for compensation to be payable in the types and proportions of currencies required to rectify the loss or damage incurred. - If the Contractor does not provide any of the policies and certificates required, the Employer may effect the insurance which the Contractor should have provided and recover the premiums the Employer has paid from payments otherwise due to the Contractor or, if no payment is due, the payment of the premiums shall be a debt due. - Alterations to the terms of an insurance shall not be made without the approval of the Project Manager. - Both parties shall comply with any conditions of the insurance policies. - The policies which are in the joint names of the Contractor and the Employer shall contain a clause to include a waiver of subrogation of the Contractor's rights to the insurance carrier against the Employer. |
| - Site Data | - The Contractor shall be deemed to have examined any Site Data referred to in the PCC, supplemented by any information available to the Contractor. |
| - Contractor to Construct the Works | - The Contractor shall construct and install the Works in accordance with the Specifications and Drawings. |
| - The Works to Be Completed by the Intended Completion Date | - The Contractor may commence execution of the Works on the Start Date and shall carry out the Works in accordance with the Program submitted by the Contractor, as updated with the approval of the Project Manager, and complete them by the Intended Completion Date. |
| - Approval by the Project Manager | - The Contractor shall submit Specifications and Drawings showing the proposed Temporary Works to the Project Manager, for his approval. - The Contractor shall be responsible for design of Temporary Works. - The Project Manager’s approval shall not alter the Contractor’s responsibility for design of the Temporary Works. - The Contractor shall obtain approval of third parties to the design of the Temporary Works, where required. - All Drawings prepared by the Contractor for the execution of the temporary or permanent Works, are subject to prior approval by the Project Manager before this use. |
| - Health and Safety | - The Contractor shall be responsible for the health and safety of all activities on the Site. - The Contractor shall comply with the relevant legislations regarding health and safety on site, including the Occupational Safety and Health (Safety of Scaffold) Regulations 2013. - The contractor shall send to the Project Manager details of any accident as soon as practicable after its occurrence and shall maintain records and submit reports concerning health, safety and welfare of persons and damage to property, as the Project Manager may reasonably require. |
| - Discoveries | - Anything of historical or other interest or of significant value unexpectedly discovered on the Site shall be the property of the Employer. The Contractor shall notify the Project Manager of such discoveries and carry out the Project Manager’s instructions for dealing with them. |
| - Possession of the Site | - The Employer shall, after receiving the Performance security, the insurance covers and the Program for the Works all as per requirements, give possession of all parts of the Site to the Contractor within seven days for execution of works in accordance to the Program for the Works. If possession of a part is not given by the date stated in the PCC or as thereafter reviewed and agreed by the parties, the Employer shall be deemed to have delayed the start of the relevant activities, and this shall be a Compensation Event. |
| - Access to the Site | - The Contractor shall allow the Project Manager and any person authorized by the Project Manager access to the Site and to any place where work in connection with the Contract is being carried out or is intended to be carried out. |
| - Instructions | - The Contractor shall carry out all instructions of the Project Manager which comply with the applicable laws where the Site is located. - The Contractor shall permit persons appointed by the Employer to inspect the Site and/or the accounts and records of the Contractor and its sub-contractors relating to the performance of the Contract, and to have such accounts and records audited by auditors appointed by the Employer if required by the Employer. The Contractor’s attention is drawn to Sub-Clause 57.1 which provides, inter alia, that acts intended to materially impede the exercise of the inspection and audit rights provided for under Sub-Clause 22.2 constitute a prohibited practice subject to contract termination. |
| - Appointment of the Adjudicator | - The Adjudicator shall be appointed jointly by the Employer and the Contractor, at the time of the Employer’s issuance of the Letter of Acceptance. If, in the Letter of Acceptance, the Employer does not agree on the appointment of the Adjudicator, the Employer will request the Appointing Authority designated in the PCC, to appoint the Adjudicator within 14 days of receipt of such request. - Should the Adjudicator resign or die, or should the Employer and the Contractor agree that the Adjudicator is not functioning in accordance with the provisions of the Contract, a new Adjudicator shall be jointly appointed by the Employer and the Contractor. In case of disagreement between the Employer and the Contractor, within 30 days, the Adjudicator shall be designated by the Appointing Authority designated in the PCC at the request of either party, within 14 days of receipt of such request. |
| - Procedure for Disputes | - If the Contractor believes that a decision taken by the Project Manager was either outside the authority given to the Project Manager by the Contract or that the decision was wrongly taken, the decision shall be referred to the Adjudicator within 14 days of the notification of the Project Manager’s decision. - The Adjudicator shall give a decision in writing within 28 days of receipt of a notification of a dispute. - The Adjudicator shall be paid by the hour at the rate specified in the PCC, together with reimbursable expenses of the types specified in the PCC, and the cost shall be divided equally between the Employer and the Contractor, whatever decision is reached by the Adjudicator. Either party may refer a decision of the Adjudicator to an Arbitrator within 28 days of the Adjudicator’s written decision. If neither party refers the dispute to arbitration within the above 28 days, the Adjudicator’s decision shall be final and binding. - The arbitration shall be conducted in accordance with the arbitration procedures published by the institution named and in the place specified in the PCC. |

B.  Time Control

| - Program | - Within the time stated in the PCC, after the date of the Letter of Acceptance, the Contractor shall submit to the Project Manager for approval a Program showing the general methods, arrangements, order, and timing for all the activities in the Works. In the case of a lump sum contract, the activities in the Program shall be consistent with those in the Activity Schedule. - An update of the Program shall be a program showing the actual progress achieved on each activity and the effect of the progress achieved on the timing of the remaining work, including any changes to the sequence of the activities. - The Contractor shall submit to the Project Manager for approval an updated Program at intervals no longer than the period stated in the PCC. If the Contractor does not submit an updated Program within this period, the Project Manager may withhold the amount stated in the PCC from the next payment certificate and continue to withhold this amount until the next payment after the date on which the overdue Program has been submitted. In the case of a lump sum contract, the Contractor shall provide an updated Activity Schedule within 14 days of being instructed to by the Project Manager. - The Project Manager’s approval of the Program shall not alter the Contractor’s obligations. The Contractor may revise the Program and submit it to the Project Manager again at any time. A revised Program shall show the effect of Variations and Compensation Events. |
| --- | --- |

| - Extension of the Intended Completion Date | - The Project Manager shall extend the Intended Completion Date if a Compensation Event(as defined in GCC 41) occurs or a Variation is issued which makes it impossible for Completion to be achieved by the Intended Completion Date without the Contractor taking steps to accelerate the remaining work, which would cause the Contractor to incur additional cost. - The Project Manager shall decide whether and by how much to extend the Intended Completion Date within 21 days of the Contractor asking the Project Manager for a decision upon the effect of a Compensation Event or Variation and submitting full supporting information. If the Contractor has failed to give early warning of a delay or has failed to cooperate in dealing with a delay, the delay by this failure shall not be considered in assessing the new Intended Completion Date. |
| --- | --- |
| - Acceleration | - When the Employer wants the Contractor to finish before the Intended Completion Date, the Project Manager shall obtain priced proposals for achieving the necessary acceleration from the Contractor. If the Employer accepts these proposals, the Intended Completion Date shall be adjusted accordingly and confirmed by both the Employer and the Contractor. - If the Contractor’s priced proposals for an acceleration are accepted by the Employer, they are incorporated in the Contract Price and treated as a Variation. |
| - Delays Ordered by the Project Manager | - The Project Manager may instruct the Contractor to delay the start or progress of any activity within the Works. |
| - Management Meetings | - Either the Project Manager or the Contractor may require the other to attend a management meeting. The business of a management meeting shall be to review the plans for remaining work and to deal with matters raised in accordance with the early warning procedure. - The Project Manager shall record the business of management meetings and provide copies of the record to those attending the meeting and to the Employer. The responsibility of the parties for actions to be taken shall be decided by the Project Manager either at the management meeting or after the management meeting and stated in writing to all who attended the meeting. |

| - Early Warning | - The Contractor shall warn the Project Manager at the earliest opportunity of specific likely future events or circumstances that may adversely affect the quality of the work, increase the Contract Price, or delay the execution of the Works. The Project Manager may require the Contractor to provide an estimate of the expected effect of the future event or circumstance on the Contract Price and Completion Date. The estimate shall be provided by the Contractor as soon as reasonably possible. - The Contractor shall cooperate with the Project Manager in making and considering proposals for how the effect of such an event or circumstance can be avoided or reduced by anyone involved in the work and in carrying out any resulting instruction of the Project Manager. |
| --- | --- |

C.  Quality Control

| - Identifying Defects | - The Project Manager shall check the Contractor’s work and notify the Contractor of any Defects that are found. Such checking shall not affect the Contractor’s responsibilities. The Project Manager may instruct the Contractor to search for a Defect and to uncover and test any work that the Project Manager considers may have a Defect. |
| --- | --- |
| - Tests | - If the Project Manager instructs the Contractor to carry out a test not specified in the Specification to check whether any work has a Defect and the test shows that it does, the Contractor shall pay for the test and any samples. If there is no Defect, the test shall be a Compensation Event. |
| - Correction of Defects | - The Project Manager shall give notice to the Contractor of any Defects before the end of the Defects Liability Period, which begins at Completion, and is defined in the PCC. The Defects Liability Period shall be extended for as long as Defects remain to be corrected. - Every time notice of a Defect is given, the Contractor shall correct the notified Defect within the length of time specified by the Project Manager’s notice. |
| - Uncorrected Defects | - If the Contractor has not corrected a Defect within the time specified in the Project Manager’s notice, the Project Manager shall assess the cost of having the Defect corrected, and the Contractor shall pay this amount. |

D.  Cost Control

| - Contract Price | - In the case of an admeasurement contract, the Bill of Quantities shall contain priced items for the Works to be performed by the Contractor. The Bill of Quantities is used to calculate the Contract Price. The Contractor will be paid for the quantity of the work accomplished at the rate in the Bill of Quantities for each item. - In the case of a lump sum contract, the Activity Schedule shall contain the priced activities for the Works to be performed by the Contractor. The Activity Schedule is used to prepare interim valuations of works done. Any errors or inconsistencies including front loading detected in the Activity Schedule at any time during the execution of the project shall be resolved as directed as by the Project Manager. |
| --- | --- |
| - Changes in the Contract Price | - In the case of an admeasurement contract: - If the final quantity of the work done differs from the quantity in the Bill of Quantities for the particular item by more than 25 percent, provided the change exceeds 1 percent of the Initial Contract Price, the Project Manager shall adjust the rate to allow for the change. - The Project Manager shall not adjust rates from changes in quantities if thereby the Initial Contract Price is exceeded by more than 15 percent, except with the prior approval of the Employer. - If requested by the Project Manager, the Contractor shall provide the Project Manager with a detailed cost breakdown of any rate in the Bill of Quantities. - In the case of a lump sum contract, the Activity Schedule shall be amended by the Contractor to accommodate changes of Program or method of working made at the Contractor’s own discretion. Prices in the Activity Schedule shall not be altered when the Contractor makes such changes to the Activity Schedule. |
| - Variations | - All Variations shall be included in updated Programs, and, in the case of a lump sum contract, also in the Activity Schedule, produced by the Contractor. - The Contractor shall provide the Project Manager with a quotation for carrying out the Variation when requested to do so by the Project Manager. The Project Manager shall assess the quotation, which shall be given within seven (7) days of the request or within any longer period stated by the Project Manager and before the Variation is ordered. - If the Contractor’s quotation is unreasonable, the Project Manager may order the Variation and make a change to the Contract Price, which shall be based on the Project Manager’s own forecast of the effects of the Variation on the Contractor’s costs. - If the Project Manager decides that the urgency of varying the work would prevent a quotation being given and considered without delaying the work, no quotation shall be given and the Variation shall be treated as a Compensation Event. - The Contractor shall not be entitled to additional payment for costs that could have been avoided by giving early warning. - In the case of an admeasurement contract, if the work in the Variation corresponds to an item description in the Bill of Quantities and if, in the opinion of the Project Manager, the quantity of work above the limit stated in Sub-Clause 38.1 or the timing of its execution do not cause the cost per unit of quantity to change, the rate in the Bill of Quantities shall be used to calculate the value of the Variation. If the cost per unit of quantity changes, or if the nature or timing of the work in the Variation does not correspond with items in the Bill of Quantities, the quotation by the Contractor shall be in the form of new rates for the relevant items of work. |
| - Cash Flow Forecasts | - When the Program, or, in the case of a lump sum contract, the Activity Schedule, is updated, the Contractor shall provide the Project Manager with an updated cash flow forecast. The cash flow forecast shall include different currencies, as defined in the Contract, converted as necessary using the Contract exchange rates. |
| - Payment Certificates | - The Contractor shall submit to the Project Manager monthly statements, with supporting documents of the estimated value of the work executed less the cumulative amount certified previously. - The Project Manager shall check the Contractor’s monthly statement and certify the amount to be paid to the Contractor within 21 days after receiving the statement and supporting documents. - The value of work executed shall be determined by the Project Manager. - The value of work executed shall comprise: - In the case of an admeasurement contract, the value of the quantities of work in the Bill of Quantities that have been completed; or - In the case of a lump sum contract, the value of work executed shall comprise the value of completed activities in the Activity Schedule. - The value of work executed shall include the valuation of Variations and Compensation Events. - The Project Manager may exclude any item certified in a previous certificate or reduce the proportion of any item previously certified in any certificate in the light of later information. An interim certificate shall not be deemed to indicate the Project Manager’s acceptance, approval, consent or satisfaction of the work. - Unless otherwise specified in the SPCC Interim Payment may be made for Plant and Material delivered on site ready for incorporation within reasonable period of time in the permanent works, subject to the Contractor transferring ownership to the Employer and providing, where applicable, the right of the transfer of ownership vested upon the Contractor by its supplier. Notwithstanding the transfer of ownership the responsibility for care and custody thereof together with the risk of loss or damage thereto shall remain with the Contractor until taking over of the works or part thereof in which such Plant and Materials are incorporated and shall make good at its own cost any loss or damage that may occur to the works or part thereof from any cause whatsoever during such period prior to the taking over. |
| - Payments | - Payments shall be adjusted for deductions for advance payments and retention. The Employer shall pay the Contractor the amounts certified by the Project Manager within 21 days of the date of each certificate but not later than 42 days after the Project Manager has received a statement with supporting documents from the Contractor. If the Employer makes a late payment, the Contractor shall be paid interest on the late payment in the next payment irrespective of the date on which any interim payment is issued. Interest shall be calculated from the date by which the payment should have been made up to the date when the late payment is made at the prevailing rate of interest at the legal rate for each of the currencies in which payments are made. The contractor shall be entitled to this payment without formal notice or certification, and without prejudice to any other right or remedy. - If an amount certified is increased in a later certificate or as a result of an award by the Adjudicator or an Arbitrator, the Contractor shall be paid interest upon the delayed payment as set out in this clause. Interest shall be calculated from the date upon which the increased amount would have been certified in the absence of dispute. - Unless otherwise stated, all payments and deductions shall be paid or charged in the proportions of currencies comprising the Contract Price. - Items of the Works for which no rate or price has been entered in shall not be paid for by the Employer and shall be deemed covered by other rates and prices in the Contract. - The contractor (if VAT Registered) shall be paid VAT upon submission of a VAT invoice. |
| - Compensation Events | - The following shall be Compensation Events: - The Employer does not give access to a part of the Site by the Site Possession Date pursuant to GCC Sub-Clause 20.1. - The Employer modifies the Schedule of Other Contractors in a way that affects the work of the Contractor under the Contract. - The Project Manager orders a delay or does not issue Drawings, Specifications, or instructions required for execution of the Works on time. - The Project Manager instructs the Contractor to uncover or to carry out additional tests upon work, which is then found to have no Defects. - The Project Manager unreasonably does not approve a subcontract to be let. - Ground conditions are substantially more adverse than could reasonably have been assumed before issuance of the Letter of Acceptance from the information issued to bidders (including the Site Investigation Reports), from information available publicly and from a visual inspection of the Site. - The Project Manager gives an instruction for dealing with an unforeseen condition, caused by the Employer, or additional work required for safety or other reasons. - Other contractors, public authorities, utilities, or the Employer does not work within the dates and other constraints stated in the Contract, and they cause delay or extra cost to the Contractor. - The advance payment is delayed. - The effects on the Contractor of any of the Employer’s Risks. - The Project Manager unreasonably delays issuing a Certificate of Completion. - In situations of Force Majeure which makes the contractor’s performance of its obligations under the Contract impossible or so impractical as to be considered impossible under the circumstances. Such events shall be limited to: - reason of any exceptionally adverse weather conditions (as specified in the BDS) and - reason of civil commotion, strike or lockout affecting any of the trades employed upon the Works or any of the trades engaged in the preparation, manufacture or transportation of any of the goods or materials required for the Works. - If a Compensation Event would cause additional cost or would prevent the work being completed before the Intended Completion Date, the Contract Price shall be increased and/or the Intended Completion Date shall be extended. The Project Manager shall decide whether and by how much the Contract Price shall be increased and whether and by how much the Intended Completion Date shall be extended. - As soon as information demonstrating the effect of each Compensation Event upon the Contractor’s forecast cost has been provided by the Contractor, it shall be assessed by the Project Manager, and the Contract Price shall be adjusted accordingly. If the Contractor’s forecast is deemed unreasonable, the Project Manager shall adjust the Contract Price based on the Project Manager’s own forecast. The Project Manager shall assume that the Contractor shall react competently and promptly to the event. - The Contractor shall not be entitled to compensation to the extent that the Employer’s interests are adversely affected by the Contractor’s not having given early warning or not having cooperated with the Project Manager. |
| - Tax | - The Project Manager shall adjust the Contract Price if taxes, duties, and other levies are changed between the date 28 days before the submission of bids for the Contract and the date of the last Completion certificate. The adjustment shall be the change in the amount of tax payable by the Contractor, provided such changes are not already reflected in the Contract Price or are a result of GCC Clause 44. |
| - Currencies | - Where payments are made in currencies other than the currency of the Employer’s country specified in the PCC, the exchange rates used for calculating the amounts to be paid shall be the exchange rates stated in the Contractor’s Bid. |
| - Price Adjustment | - Prices shall be adjusted for fluctuations in the cost of inputs only if provided for in the PCC. If so provided, the amounts certified in each payment certificate, before deducting for Advance Payment, shall be adjusted by applying the respective price adjustment factor to the payment amounts due in each currency. A separate formula of the type indicated below applies to each Contract currency: Pc = Ac + Bc Imc/Ioc where: Pc is the adjustment factor for the portion of the Contract Price payable in a specific currency “c.” Ac and Bc are coefficients specified in the PCC, representing the nonadjustable and adjustable portions, respectively, of the Contract Price payable in that specific currency “c;” and Imc is the index prevailing at the end of the month being invoiced and Ioc is the index prevailing 28 days before Bid opening for inputs payable; both in the specific currency “c.” - If the value of the index is changed after it has been used in a calculation, the calculation shall be corrected and an adjustment made in the next payment certificate. The index value shall be deemed to take account of all changes in cost due to fluctuations in costs. |
| - Retention | - The Employer shall retain from each payment due to the Contractor the proportion stated in the PCC until Completion of the whole of the Works. - Upon the issue of a Certificate of Completion of the Works by the Project Manager, in accordance with GCC 53.1, half the total amount retained shall be repaid to the Contractor and half when the Defects Liability Period has passed and the Project Manager has certified that all Defects notified by the Project Manager to the Contractor before the end of this period have been corrected. The Contractor may substitute retention money with an “on demand” Bank/Insurance guarantee. |
| - Liquidated Damages | - The Contractor shall pay liquidated damages to the Employer at the rate per day stated in the PCC for each day that the Completion Date is later than the Intended Completion Date. The total amount of liquidated damages shall not exceed the amount defined in the PCC. This amount may be included as a deduction in the contract price and payment certificate. Payment of liquidated damages shall not affect the Contractor’s liabilities. - If the Intended Completion Date is extended after liquidated damages have been paid, the Project Manager shall correct any overpayment of liquidated damages by the Contractor by adjusting the next payment certificate. The Contractor shall be paid interest on the overpayment, calculated from the date of payment to the date of repayment, at the rates specified in GCC Sub-Clause 40.1. |
| - Bonus | - The Contractor shall be paid a Bonus calculated at the rate per calendar day stated in the PCC for each day (less any days for which the Contractor is paid for acceleration) that the Completion is earlier than the Intended Completion Date. The Project Manager shall certify that the Works are complete, although they may not be due to be complete. |
| - Advance Payment | - The Employer shall make advance payment to the Contractor of the amounts stated in the PCC by the date stated in the PCC, against provision by the Contractor of an Unconditional Bank/Insurance Guarantee in a form and by a bank/insurance company acceptable to the Employer in amounts and currencies equal to the advance payment. The Guarantee shall remain effective until the advance payment has been repaid, but the amount of the Guarantee shall be progressively reduced by the amounts repaid by the Contractor. Interest shall not be charged on the advance payment. - The Contractor is to use the advance payment only to pay for Equipment, Plant, Materials, and mobilization expenses required specifically for execution of the Contract. The Contractor shall demonstrate that advance payment has been used in this way by supplying copies of invoices or other documents to the Project Manager. - The advance payment shall be repaid by deducting proportionate amounts from payments otherwise due to the Contractor, following the schedule of completed percentages of the Works on a payment basis. No account shall be taken of the advance payment or its repayment in assessing valuations of work done, Variations, price adjustments, Compensation Events, Bonuses, or Liquidated Damages. |
| - Securities | - The Performance Security shall be provided to the Employer within 28 days of the receipt of the Letter of Acceptance and shall be issued in an amount specified in the PCC, by a local bank or local insurance company and denominated in the types and proportions of the currencies in which the Contract Price is payable. The Performance Security shall be valid until a date 21 days from the date of issue of the Defects Liability Certificate. The employer shall return the performance security within 21 days after receipt of a copy of the Defects Liability Certificate. - (a)Where the contractor has benefitted from the application of the Margin of Preference for employment of local manpower, it shall: - in the execution of the contract, fulfill its obligation of maintaining local manpower force for 80 % or more of the man-days deployed in the execution of the Works with which it satisfied the criteria of eligibility for being awarded the contract in application of the Margin of Preference; and - concurrently with the above performance security, provide a preference security to guarantee it will fulfill its obligation in that respect. (b) For contracts above Rs 100M, the preference security shall be in the form of an “on demand” bank/insurance guarantee for an amount in a convertible currency equivalent to the difference between its bid price and the bid price of the lowest bid if the Margin of Preference was not applicable. It shall be issued by a commercial bank/insurance company located in the Republic of Mauritius. (c) For contracts up to 100M, the public body shall either retain money from progressive payments to constitute the preference security or request a security in the form of a bank/insurance guarantee at the selected bidder’s option. (d) The preference security shall be valid until the Contractor has completed the Works and a Completion Certificate has been issued by the Employer’s Representative as per GCC 53. (e) The cost of providing the security shall be borne by the Contractor. - Where a Preference Security is applicable: - the Employer’s Representative shall monitor the employment of local manpower throughout the execution of the contract and shall from time to time request a report from the contractor on the percentage of total men-days deployed using local manpower. - the Contractor shall submit the local manpower employment reports as often as it is reasonably requested by the Employer’s Representative. - the Employer’s and Contractor’s representatives shall consult each other to ensure that the Contractor’s obligation towards local manpower employment is met during the Works execution. - At the time of works completion, the Contractor shall submit a certified audited report to the Employer to substantiate the actual percentage of local manpower employed throughout the execution of the works. - The preference security shall be forfeited by the employer in case of failure on the part of the contractor to employ at least 80% of the local manpower in the execution of the Works. |
| - Dayworks | - If applicable, the Dayworks rates in the Contractor’s Bid shall be used only when the Project Manager has given written instructions in advance for additional work to be paid for in that way. - All work to be paid for as Dayworks shall be recorded by the Contractor on forms approved by the Project Manager. Each completed form shall be verified and signed by the Project Manager within two days of the work being done. - The Contractor shall be paid for Dayworks subject to obtaining signed Dayworks forms. |
| - Cost of Repairs | - Loss or damage to the Works or Materials to be incorporated in the Works between the Start Date and the end of the Defects Correction periods shall be remedied by the Contractor at the Contractor’s cost if the loss or damage arises from the Contractor’s acts or omissions. |
| - Labour Clause | - (a) The rates of remuneration and other conditions of work of the employees of the Contractor shall not be less favourable than those established for work of the same character in the trade concerned- (i) by collective agreement applying to a substantial proportion of the workers and employers in the trade concerned; (ii) by arbitration awards; or (iii) by Remuneration Regulations made under the Employment Relation Act 2008. (b) Where remuneration and conditions of work are not regulated in a manner referred to at (a) above, the rates of the remuneration and other conditions of work shall be not less favourable than the general level observed in the trade in which the contractor is engaged by employers whose general circumstances are similar. - No Contractor shall be entitled to any payment in respect of work performed in the execution of the contract unless he has, together with his claim for payment, filed a certificate: (a) stating the rates of remuneration and hours of work of the various categories of employees employed in the execution of the contracts; (b) stating whether any remuneration payable in respect of work done is due; (c) containing such other information as the Chief Executive Officer of the Public Body administering the contract may require to satisfy himself that the provisions under this clause have been complied with. - Where the Chief Executive Officer of the Public Body administering the contract is satisfied that remuneration is still due to an employee employed under this contract at the time the claim for payment is filed under subsection 4.3, he may, unless the remuneration is sooner paid by the Contractor, arrange for the payment of the remuneration out of the money payable under this contract. - Every Contractor shall display a copy of this clause of the contract at the place at which the work required by the contract is performed. |

E.  Finishing the Contract

| - Completion | - The Contractor shall request the Project Manager to issue a Certificate of Completion of the Works, and the Project Manager shall do so upon deciding that the whole of the Works is completed. - The Certificate of Completion shall be issued within 14 days from date of completion of the works. |
| --- | --- |
| - Taking Over | - The Employer shall take over the Site and the Works within seven days of the Project Manager’s issuing a certificate of Completion. |
| - Final Account | - The Contractor shall supply the Project Manager with a detailed account of the total amount that the Contractor considers payable under the Contract before the end of the Defects Liability Period. The Project Manager shall issue a Defects Liability Certificate and certify any final payment that is due to the Contractor within 56 days of receiving the Contractor’s account if it is correct and complete. If it is not, the Project Manager shall issue within 56 days a schedule that states the scope of the corrections or additions that are necessary. If the Final Account is still unsatisfactory after it has been resubmitted, the Project Manager shall decide on the amount payable to the Contractor and issue a payment certificate. - If the contractor has not supplied the detailed account under Sub-Clause 55.1 the Project Manager shall request the contractor to do so. If the Contractor fails to submit the detailed account within a period of 28 days, the Project Manager shall issue the Final Payment Certificate for such an amount as he fairly determines to be due. |
| - Operating and Maintenance Manuals | - If “as built” Drawings and/or operating and maintenance manuals are required, the Contractor shall supply them by the dates stated in the PCC. - If the Contractor does not supply the Drawings and/or manuals by the dates stated in the PCC pursuant to GCC Sub-Clause 55.1, or they do not receive the Project Manager’s approval, the Project Manager shall withhold the amount stated in the PCC from payments due to the Contractor. |
| - Termination | - The Employer or the Contractor may terminate the Contract if the other party causes a fundamental breach of the Contract. - Fundamental breaches of Contract shall include, but shall not be limited to, the following: - the Contractor stops work for 28 days when no stoppage of work is shown on the current Program and the stoppage has not been authorized by the Project Manager; - the Project Manager instructs the Contractor to delay the progress of the Works, and the instruction is not withdrawn within 28 days; - the Employer or the Contractor is made bankrupt or goes into liquidation other than for a reconstruction or amalgamation; - a payment certified by the Project Manager is not paid by the Employer to the Contractor within 84 days of the date of the Project Manager’s certificate; - the Project Manager gives Notice that failure to correct a particular Defect is a fundamental breach of Contract and the Contractor fails to correct it within a reasonable period of time determined by the Project Manager; - the Contractor does not maintain a Security, which is required; - the Contractor has delayed the completion of the Works by the number of days for which the maximum amount of liquidated damages can be paid, as defined in the PCC; or - if the Contractor, in the judgment of the Employer, has engaged in corrupt or fraudulent practices in competing for or in executing the Contract, pursuant to GCC Clause 57.1. - When either party to the Contract gives notice of a breach of Contract to the Project Manager for a cause other than those listed under GCC Sub-Clause 56.2 above, the Project Manager shall decide whether the breach is fundamental or not. - Notwithstanding the above, a public body may terminate the contract for its convenience at any time upon a determination that because of changed circumstances the continuation of the contract is not in the public interest. - If the Contract is terminated, the Contractor shall stop work immediately, make the Site safe and secure, and leave the Site as soon as reasonably possible. |
| - Fraud / Corruption and Integrity Clause | - If the Employer determines that the Contractor has engaged in corrupt, fraudulent, collusive, coercive or obstructive practices, in competing for or in executing the Contract, then the Employer may, after giving 14 days notice to the Contractor, terminate the Contractor's employment under the Contract and expel him from the Site, and the provisions of Clause 57 shall apply as if such expulsion had been made under Sub-Clause 57.5 [Termination by Employer]. - Should any employee of the Contractor be determined to have engaged in corrupt, fraudulent, collusive, coercive, or obstructive practice during the execution of the Works, then that employee shall be removed in accordance with Clause 9. 58.3 For the purposes of this Sub-Clause: (i) “corrupt practice” is the offering, giving, receiving or soliciting, directly or indirectly, of anything of value to influence improperly the actions of another party; (ii) “fraudulent practice” is any act or omission, including a misrepresentation, that knowingly or recklessly misleads, or attempts to mislead, a party to obtain a financial or other benefit or to avoid an obligation; (iii) “collusive practice” is an arrangement between two or more parties designed to achieve an improper purpose, including to influence improperly the actions of another party; (iv)“coercive practice” is impairing or harming, or threatening to impair or harm, directly or indirectly, any party or the property of the party to influence improperly the actions of a party; (v) “obstructive practice” is (a) deliberately destroying, falsifying, altering or concealing of evidence material to the investigation or making false statements to investigators in order to materially impede an investigation into allegations of a corrupt, fraudulent, coercive or collusive practice; and/or threatening, harassing or intimidating any party to prevent it from disclosing its knowledge of matters relevant to the investigation or from pursuing the investigation; or (b) acts intended to materially impede the exercise of an inspection and audit rights provided for under Sub-Clause 22.2. 58.4 The Contractor shall take steps to ensure that no person acting for it or on its behalf will engage in any type of fraud and corruption during the contract execution: Transgression of the above is a serious offence and appropriate actions will be taken against such contractors. |
| - Payment upon Termination | - If the Contract is terminated because of a fundamental breach of Contract by the Contractor, the Project Manager shall issue a certificate for the value of the work done and Materials ordered less advance payments received up to the date of the issue of the certificate and less the percentage to apply to the value of the work not completed, as indicated in the PCC. Additional Liquidated Damages shall not apply. If the total amount due to the Employer exceeds any payment due to the Contractor, the difference shall be a debt payable to the Employer. - If the Contract is terminated for the Employer’s convenience or because of a fundamental breach of Contract by the Employer, the Project Manager shall issue a certificate for the value of the work done, Materials ordered, the reasonable cost of removal of Equipment, repatriation of the Contractor’s personnel employed solely on the Works, and the Contractor’s costs of protecting and securing the Works, and less advance payments received up to the date of the certificate - If the Contract is terminated the Contractor shall not be entitled to recover anticipated profits on the completion of the contract. |
| - Property | - All Materials on the Site, Plant, Equipment, Temporary Works, and Works shall be deemed to be the property of the Employer if the Contract is terminated because of the Contractor’s default. |
| - Release from Performance | - If the Contract is frustrated by the outbreak of war or by any other event entirely outside the control of either the Employer or the Contractor, the Project Manager shall certify that the Contract has been frustrated. The Contractor shall make the Site safe and stop work as quickly as possible after receiving this certificate and shall be paid for all work carried out before receiving it and for any work carried out afterwards to which a commitment was made. |

Particular Conditions of Contract

| A. General |  |
| --- | --- |
| GCC 1.1 (r) | The Employer is Sugar Industry Labour Welfare Fund 15-21, Edith Cavell Street, Port-Louis |
| GCC 1.1 (v) | The Intended Completion Date for the whole of the Works shall be 240 days from the start date. |
| GCC 1.1 (y) | The Project Manager(s) shall be the representative of the Ministry of National Infrastructure and Community Development as shall be designated by the Sugar Industry Labour Welfare Fund. |
| GCC 1.1 (aa) | The Site is located at Gokoola and is defined in drawings No. G859/SW/03 |
| GCC 1.1 (dd) | “The Start Date shall be 14 days after handing over of site. |
| GCC 1.1 (hh) | The project consists of the construction of a New Community Wellness Centre and other related works at Gokoola as described hereunder: 1. Demolition works of existing part of boundary wall, kerbs, low wall and fencing, steps, absorption pit, flower boxes as per drawings. 2.The construction of a new single storey Community Wellness Centre in reinforced concrete structure, finished with the following works; - internal and external rendering/painting, ceramic floor tiles and wall tiles, waterproofing works, pergola and false ceiling, plumbing and drainage installations works, electrical works, rain water pipes, aluminium doors and windows, burglar proofing, timber openings, interior plants and site works and other miscellaneous works described in the bid documents. 3.External services installation works comprising rainwater installation works such as catch pits, gully traps, soak aways, waste water installation works such as manholes, channel manholes, septic tank, absorption pit, water supply works, electrical main supply and electric manholes. Works shall include reinstatement of damaged underground pipes and cables and other services that may be met with. 4. Provision of all piping including water supply, water tank, waste, floor traps, connection to covered drain, soakaways, etc. as per Mechanical Engineer. 5.Hoarding shall be provided to secure contractor’s workspace and the site. Hoarding shall be to the satisfaction of the Project Architect and Project Structural Engineer. 6.Site works such as disabled parking, visitors parking, interlocking block, grass planting, CEB cubicle, pump room, garbage bins, boundary wall, green pavers, flower boxes, concrete platform for water tank, covered drains and landscaping and plants. 7.Works include reinstatement of damaged structures and finishes incidental to construction works. 8.Other works as more fully described in the drawings, specifications and other parts of the Bid document. The duration of the construction works shall be 240 Days from the date of start of works. |
| GCC 2.2 | Sectional Completions are: Not Applicable |
| GCC 2.3(i) | The following documents also form part of the Contract: Performance Security, Insurance Policies and addenda (if any). The performance security and insurance policies shall be submitted within 21 days as from the date of receipt of Letter of Acceptance, for verification by the Quantity Surveyor before the handing over of site. |
| GCC 3.1 | The language of the contract is English The law that applies to the Contract is the law of Mauritius. |
| GCC 5.1 | The Project manager may delegate any of his duties and responsibilities. |
| GCC 8.1 | Schedule of other contractors: Not Applicable |
| GCC 13.1 | Except for the cover mentioned in (d)(i) hereunder, the other insurance covers shall be in the joint names of the Contractor and the Employer and the cover shall apply separately to each insured as though a separate policy had been issued to each of the joint insured. The minimum insurance amounts shall be: (a) for the Works, Plant and Materials: (for the full amount of the works including removal of debris, professional fee etc...) (b) for loss or damage to Equipment: (for the replacement value of the equipment that the contractor intends to use on site until the taking over by the Employer. Evidence to be produced by Contractor. Delete content of Sub Clause 13.1 (c) and (d) entirely and replace by new Sub clause 13.1 (c) and (d) (i) and (ii) as follows: (c) for loss or damage to adjoining property and/or property in which the works are being carried out (except the Works, Plant, Materials, and Equipment) in connection with Contract for an amount of Rs 10,000,000 representing the value of the properties that are exposed to the action of the contractor in the execution of the works. It will extend to the property of the Procuring Entity as well). (d) for personal injury or death and damage to property - of the Contractor’s employees: [The Contractor shall take an adequate insurance cover for its employees for any claim arising in the execution of the works]. Evidence to be produced by Contractor. (ii) for injury to persons and loss or damage to property for an amount of 10 (Ten) Million Rupees representing each Party’s liability for any loss, damage, death or bodily injury which may occur to any physical property [except the Works, Plant, Materials, Equipment and damage to property insured under GCC 13.1 (a), (b) & (c)] or to any person [except for Contractor’s employees insured under GCC 13.1 (d)(i)] including the Employer and its representatives which may arise out of the Contractor’s performance of the contract This insurance shall be for a limit per occurrence of not less than the amount stated above (i.e Rs. 10 million), with no limit in number of occurrences. The ceiling for the Third Party Liability shall be for a minimum amount of Rs. 100 million, subject to a provision that this amount may be reviewed during the contract period, but will in any case be for a fixed amount. (In line with PPO Directive 56) Add the following sub-clause 13.1 (e) (e) for loss or damage to materials on-site and for which payment have been included in the Interim Payment Certificate, where applicable.) for loss or damage to materials on-site and for which payment have been included in the Interim Payment Certificate, where applicable. The Contractor shall choose to take the insurance covers indicated above as separate covers or a combination of the Contractor’s All Risks coupled with the Employer’s liability and First Loss Burglary, after approval of the Employer. All insurance covers shall be of nil or the minimum possible deductibles at sole expense of the contractor. |
| GCC 13.3 | Delete content of Sub Clause 13.3 entirely and replace by “If the Contractor does not provide any of the policies and certificates required, this may constitute a breach of the contractor’s obligations under the bid conditions and may entail forfeiture of bid security or performance security or any action by the Employer under the Bid Securing Declaration” |
| GCC 13.7 | Add the following new sub clause “13.7 – In the Event works are carried out beyond the Intended Completion Date or the Intended Completion date is extended, the contractor shall extend the Insurance policies to cover for the extended period and defects liability period. Failure on the part of the contractor to comply with the above condition may entail: - Non- certification of payment - Termination of contract - Forfeiture of the Performance security. |
| GCC 14.1 | Site Data are: There are no Site Investigation Reports for this project. Bidders are however advised to visit the site prior to submission of bid. They should acquaint themselves with the nature of the site, extent of the work, means of access, general nature of the soil and all other matters which may influence their bid. No claim due to ignorance of these factors as mentioned in the preceding paragraph shall be entertained from the contractor. |
| GCC 20.1 | The Site Possession Date(s) shall be: within Fourteen (14) days from submission and approval of Performance Security and Insurance covers. The area of the site which may be occupied by the Contractor for his use as site office or for erection of workshop etc. shall be approved by the Project Manager or his representative. |
| GCC 23.1 & GCC 23.2 | Appointing Authority for the Adjudicator: No Adjudicator shall be appointed for this Contract. |
| GCC 24. | In case a dispute of any kind arises between the Employer and the Contractor in connection with, or arising out of, the contract or the execution of works or after completion of works and whether before or after repudiation or other termination of Contract, including any dispute as to any opinion, instruction, determination, certificate or valuation of the Employer’s Representative, the matter in dispute shall, in the first place, be referred in writing to the employer’s representative, with a copy to the other party. The Employer and the Contractor shall make every effort to resolve the dispute amicably by direct informal negotiation. If, after twenty-eight (28) days, the parties have failed to resolve their dispute or difference by such mutual consultation, then either the Public Body or the Contractor may give notice to the other party of its intention to refer the matter to “ the competent courts of Mauritius” |
| GCC 24.3 | Hourly rate and types of reimbursable expenses to be paid to the Adjudicator: Not applicable. |
| GCC 24.4 | Not Applicable |
| B. Time Control |  |
| GCC 25.1 | The Contractor shall submit for approval a Program for the Works within 14 days from the date of handing over of site. Delete the words “In the case of a lump sum contract, the activities in the Program shall be consistent with those in the Activity Schedule” in line 5 of clause 25. |
| GCC 25.3 | Delete the words “In the case of a lump sum contract, the contractor shall provide an updated Activity Schedule within 14 days of being instructed to by the Project Manager” in line 7 of clause 25.3 The period between Program updates is 30 days. The amount to be withheld for late submission of an updated Program is Rs 25,000 in the next payment certificate. |
| C. Quality Control |  |
| GCC 33.1 | The Defects Liability Period is: 365 calendar days. |
| GCC 34.1 | Delete sub-clause 34.1 and replace by the following: Should any defect arise during the contractual period and up to the end of the Defects Liability Period and the Contractor fails to correct the Defect within the time specified in the Project Manager’s notice, this shall constitute a breach of the Contractor’s obligations under the contract. The Project Manager shall assess the cost of having the defect corrected and recover the money from monies due to the contractor or from the Performance Security. |
| D. Cost Control |  |
| GCC 35.2 | Delete “is” and replace by “may be “after line 3 in clause 35.2 |
| GCC 35.3 | Add new sub clause “35.3-Where a work is implied in the drawings or specifications or description of works and not itemized in the Bills of Quantities, any such work shall be deemed to have been priced elsewhere in the contract price” |
| GCC 35.4 | Add new sub clause“35.4 -Any prices in the Bills of Quantities shall be fully inclusive for the finished works described under the respective work item and drawings and/ or specifications and scope of works” |
| GCC 36.2 | Delete sub Clause 36.2 entirely |
| GCC 37.2 | Add “Omissions and additions shall be measured and valued at Bill of Quantities rates or if such rates are not available at fair rates and prices, having regards to current market prices. The contractor shall supply all information required by the Project Manager to enable him to value a variation” after line 6 of clause 37.2 |
| GCC 39.7 | Interim Payment for Plant and Material on site is not applicable. |
| GCC 40.1 | Amend clause 40.1 by replacing 21 days by 7 and 42 days by 28 days. |
| GCC 41.1 (l) | The term “exceptionally adverse weather conditions” is hereby defined as any one of the following events: - 100 mm rainfall or above recorded in one day at the nearest rain station; - An official declaration of “Torrential Rain” by the Meteorological Department of Mauritius; and (3) Cyclone warning Class III or IV. |
| GCC 43.1 | The currency of the Employer’s country is: Mauritian Rupees. |
| GCC 44.1 | The Contract is not subject to price adjustment. |
| GCC 45.1 | GCC Clause 45 is not applicable. |
| GCC 46.1 | The liquidated damages for the whole of the Works are Rs. 17,000 per day. The maximum amount of liquidated damages for the whole of the Works is 3% of the Contract price. |
| GCC 47.1 | The Bonus for the whole of the Works is not applicable. |
| GCC 48.1 | The Advance Payments shall be: 10 % maximum of the contract price less contingency sum and shall be paid to the contractor no later than Seven (7) days from the date of issue of certificate. The Advance Payment shall be recovered through contractor’s running account bills at the rate of 12.5 % of the gross value of works done including materials on site. |
| GCC 49.1 | The Performance Security amount is 10 % of the contract price in the form of a Bank Guarantee as per the format in Section VIII. and shall be valid up to a date twenty-one after the end of the Defects Liability Period (DLP). Where the Performance Security expire before the date twenty-one days after the end of the DLP, the contractor shall extend the Performance Security to cover the period up to the latest date of the DLP plus twenty-one days . Failure to extend the validity of the Performance Security twenty-one days prior to its expiry may entail forfeiture of the full amount of the Performance Security. Note: The Contractor shall execute all work required to remedy defects or damage, as may be notified to him by or on behalf of the employer, on or before the expiry date of the DLP or any extended date if a defect or damage cannot be remedied by the expiry date, all at the risk and cost of the contractor. |
| E. Finishing the Contract |  |
| GCC 56.1 | The date by which operating and maintenance manuals are required is : the date of completion. The date by which “as built” drawings is required is: the date of completion. |
| GCC 56.2 | The amount to be withheld for failing to produce “as built” drawings and/or operating and maintenance manuals by the date required in GCC 56.1 is Rs. 25,000. |
| GCC 57.2 (g) | The maximum number of days is: 60 days |
| GCC 59.1 | The percentage to apply to the value of the work not completed, representing the Employer’s additional cost for completing the Works, is 20% |

Section V- Contract forms

Performance Security

...............................Bank/Insurance Company’s Name and Address of Issuing Branch or Office….....................................................

Beneficiary: .............................................Name and Address of Public Body................................................................

Date..............

PERFORMANCE GUARANTEE No.: ..........................................................................................

We have been informed that ..................................[name of the Contractor] ............................ (hereinafter called "the Contractor") has entered into Contract No.............[reference number of the Contract] ............ dated........ with you, for the execution of ......................................[name of Contract and brief description of Works] ....................(hereinafter called "the Contract").

Furthermore, we understand that, according to the conditions of the Contract, a performance security is required.

At the request of the Contractor, we ................................. [name of Bank/Insurance Company] ..................hereby irrevocably undertake to pay you any sum or sums not exceeding in total an amount of .......... [amount in figures (amount in words)] ........................................... such sum being payable in the types and proportions of currencies in which the Contract Price is payable, upon receipt by us of your first demand in writing accompanied by a written statement stating that the Contractor is in breach of its obligation(s) under the Contract, without your needing to prove or to show grounds for your demand or the sum specified therein.

This guarantee shall expire and returned to us not later than twenty- one days from the date of issuance of the Defects Liability Certificate, calculated based on a copy of such Certificate which shall be provided to us, or on the................................day of .................................., .................., whichever occurs first.  Consequently, any demand for payment under this guarantee must be received by us at this office on or before that date.

………....................................................Seal of bank/Insurance Guarantee and

Signature(s).............................................................

Advance Payment Security

[Bank’s/ Insurance Company’s Name, and Address of Issuing Branch or Office]

Beneficiary: 	[Name and Address of Employer]

Date:

Advance Payment Guarantee No.:

We have been informed that . . .. . [name of the Contractor] . . . . .  (hereinafter called “the Contractor”) has entered into Contract No. . . . . . [reference number of the Contract] . . . . .   dated . . . . . .. . with you, for the execution of . . . . . . [name of contract and brief description of Works] . . . . .  (hereinafter called “the Contract”).

Furthermore, we understand that, according to the Conditions of the Contract, an advance payment in the sum . . . . . [name of the currency and amount in figures] 1. . . . . . (. . .. . [amount in words] . . . . .  ) is to be made against an advance payment guarantee.

At the request of the Contractor, we . . .. . [name of the Bank/Insurance Company] . . . . .  hereby irrevocably undertake to pay you any sum or sums not exceeding in total an amount of . . .. . [name of the currency and amount in figures] *. . . . . . (. . . . . [amount in words] . . . . .  ) upon receipt by us of your first demand in writing accompanied by a written statement stating that the Contractor is in breach of its obligation under the Contract because the Contractor used the advance payment for purposes other than the costs of mobilization in respect of the Works.

It is a condition for any claim and payment under this guarantee to be made that the advance payment referred to above must have been received by the Contractor on its account number . . .. . [Contractor’s account number] . . . . .   at . . .. . [name and address of the Bank/Insurance Company] . . . . .  .

The maximum amount of this guarantee shall be progressively reduced by the amount of the advance payment repaid by the Contractor as indicated in copies of interim statements or payment certificates which shall be presented to us.  This guarantee shall expire, at the latest, upon our receipt of a copy of the interim payment certificate indicating that eighty (80) percent of the Contract Price has been certified for payment, or on the . . . day of . . . . . .. , . . . . . 2, whichever is earlier.  Consequently, any demand for payment under this guarantee must be received by us at this office on or before that date.

. . . . . . . . . . . . . . [Seal of Bank/Insurance Company and Signature(s)] . . . . . . . . . . . . . .

Note –

All italicized text is for guidance on how to prepare this demand guarantee and shall be deleted from the final document.

1	The Guarantor shall insert an amount representing the amount of the advance payment denominated either in the currency(ies) of the advance payment as specified in the Contract, or in a freely convertible currency acceptable to the Employer.

2	Insert the expected expiration date of the Time for Completion.  The Employer should note that in the event of an extension of the time for completion of the Contract, the Employer would need to request an extension of this guarantee from the Guarantor.  Such request must be in writing and must be made prior to the expiration date established in the guarantee. In preparing this guarantee, the Employer might consider adding the following text to the form, at the end of the penultimate paragraph:  “The Guarantor agrees to a one-time extension of this guarantee for a period not to exceed [six months][one year], in response to the Employer’s written request for such extension, such request to be presented to the Guarantor before the expiry of the guarantee.

Letter of Acceptance

[ on letterhead paper of the Employer]

. . . . . . . [date]. . . . . ..

To:	. . . . . . . . ..  [ name and address of the Contractor] . . . . . . . . ..

Subject:	. . . . . . . . ..   [Notification of Award Contract No].  . . . . . . . . . .

This is to notify you that your Bid dated . . . . [insert date] . . . .  for execution of the . . . . . . . . . .[insert name of the contract and identification number, as given in the Appendix to Bid] . . . . . . . . . . for the Accepted Contract Amount of .Rs . . . . . . . .[insert amount in numbers and words and name of currency], exclusive of VAT, as corrected and modified in accordance with the Instructions to Bidders is hereby accepted by (insert name of Public Body).

You are requested to furnish the Performance Security in accordance with the General Conditions of Contract, using for that purpose of the Performance Security Form included in Section   V (Contract Forms) of the Bidding Document.

Authorized Signature:

Name and Title of Signatory:

Name of Agency:

Attachment:  Contract Agreement

Contract Agreement

THIS AGREEMENT made the . . . . . .day of . . . . . . . . . . . . . . . . ., . . . . . . ., between . . . . . [name of the Employer]. . . . .. . . . . (hereinafter “the Employer”), of the one part, and . . . . . [name of the Contractor]. . . . .(hereinafter “the Contractor”), of the other part:

WHEREAS the Employer desires that the Works known as . . . . . [name of the Contract]. . . . .should be executed by the Contractor, and has accepted a Bid by the Contractor for the execution and completion of these Works and the remedying of any defects therein,

The Employer and the Contractor agree as follows:

1.	In this Agreement words and expressions shall have the same meanings as are respectively assigned to them in the Contract documents referred to.

2.	The following documents shall be deemed to form and be read and construed as part of this Agreement. This Agreement shall prevail over all other Contract documents.

    - the Letter of Acceptance

    - the Bid

    - the Addenda Nos . . . . . [insert addenda numbers if any]. . . . .

    - the Appendix to the General Conditions of Contract

    - the General Conditions of Contract;

    - the Specification

    - the Drawings; and

    - the completed Schedules,

3.	In consideration of the payments to be made by the Employer to the Contractor as indicated in this Agreement, the Contractor hereby covenants with the Employer to execute the Works and to remedy defects therein in conformity in all respects with the provisions of the Contract.

4.	The Employer hereby covenants to pay the Contractor in consideration of the execution and completion of the Works and the remedying of defects therein, the Contract Price or such other sum as may become payable under the provisions of the Contract at the times and in the manner prescribed by the Contract.

5.	(a) Notwithstanding anything to the contrary in this agreement, [Name of appointed Contractor] agrees to indemnify and hold harmless the Sugar Industry Labour Welfare Fund from any claim brought by or on behalf of third parties against it, its préposés and/or agents, for any loss or damage caused to third parties or on their behalf by the acts and omission of [Name of appointed Contractor] or its employees, préposés and/or agents during the execution of the works pursuant to the agreement.

(b) Notwithstanding anything to the contrary in this agreement, the Sugar Industry Labour Welfare Fund shall be entitled to claim from [Name of appointed Contractor] such loss and damages caused to it by the acts or omissions of [Name of appointed Contractor], its employees, préposés and/or agents.

IN WITNESS whereof the parties hereto have caused this Agreement to be executed in accordance with the laws of Mauritius on the day, month and year indicated above.

| Signed by: |  | Signed by: |  |
| --- | --- | --- | --- |
| for and on behalf of the Employer |  | for and on behalf the Contractor |  |
| in the presence of: |  | in the presence of: |  |
| Witness, Name, Signature, Address, Date |  | Witness, Name, Signature, Address, Date |  |

Appendix I– Standard Specifications

GOVERNMENT OF MAURITIUS

STANDARD SPECIFICATIONS

MINISTRY OF WORKS

PHOENIX

STANDARD SPECIFICATIONS

INDEX

Description										Pages

1.  Concrete blocklayer								2

2.  Mason										4

3.  Carpenter and joinery								5

4.  Ironmonger, smith and metal worker						8

5.  Pavior										9

6.  Plasterer and wall tiler								11

7.  Glazier										13

8.  Painter and decorator								14

9.  Plumber										16

10.Drainlayer										 19

11. Roads and footpaths								 21

SPECIFICATIONS FOR REINFORCED CONCRETE WORK

12. General										-

13. Excavation										22

14. Concrete work									24

15. Concrete strengths									26

16. Construction joints								30

17. Expansion/contraction joint							31

18. Water bars										31

19. Embedded items in concrete							32

20. Placing concrete									32

21. Compaction of concrete								34

22. Curing and protection								35

23. Faulty concrete									35

24. Reinforcements									35

25. Chase, holes etc in concrete							37

26. Position of electrical conduit							38

27. Formwork										38

28. Precast concrete									40

29. Composite floor slabs								41

30. Notes concerning measurement and pricing					42

31. Index for reinforced concrete work						44

- 2 -

CONCRETE  BLOCKLAYER

Concrete blocks 	Concrete blocks for walling shall comply with B.S 2028 Type A (for load bearing walls) and of compressive strength not less than:

Cavern of 12 blocks ……..500 lbs/sq.in

Gross area

Lowest individual block ….375 lbs/sq.in

Gross area

Blocks for non load bearing walls are to be class B blocks.

Blocks shall be hollow two-hole type and shall be cured for not less than 28 days before they are used in the works.  The Contractor shall supply a certificate from the supplier for each consignment of block received to the effect that the blocks meet the requirements and strength of the latest relevant B.S.  Any block for which a certificate cannot be produced will be condemned and must be removed from site.  All blocks supplied shall	be of the same height and blocks of similar dimensions will not be 	accepted.  Half length blocks and specials shall also be provided as specified or required to break bond.

Mortar	Mortar to be used for all Type A blockwall shall be composed of 1 part of cement to 3 parts of sand.  Mortar for Type B blockwork shall be composed of one part of Portland cement, one part lime, and five parts of sand.  All mortar shall be measured in specially prepared gauge boxes 	and thoroughly mixed dry or clean and water tight mixing platforms, with water added from a fine rose until all parts are completely incorporated and brought to a proper consistency.

All mortar must be used within thirty minutes of mixing.  No partially or Wholly set mortar will be allowed to be used or re-mixed.

Setting and jointing	All blocks shall be lightly wetted immediately before being bedded and jointed to minimise absorption of water from the mortar.

Blocks are to be well buttered with mortar as previously specified.  The blocks shall be laid fir-faces on the outside face, in stretcher bond with 10mm, thick, full, flused up and grouted solid joints.  The joints shall not vary by more than 3mm and four consecutive joints shall not exceed 38mm and four consecutive joints shall not exceed 38mm.  Joints shall be raked out where surfaces of walling are to be plastered.

Laying of blocks	All walls throughout the work shall be carried up evenly in courses, no part being allowed to be carried up more than 900 mm. higher at one time than any other part and in such cases the joining shall be made in long steps so as to prevent cracks arising and all walls shall be levelled around at each floor.

All put log holes shall be carefully, properly and completely filled up on completion of walling work.

- 3 -

All walling shall be properly protected while mortar is setting.

Walls shall be kept thoroughly wet for at least three days or for such

longer period of time as the Architect may direct.  Walls exposed to the sun shall be protected with a sacking which shall be kept wet.

Fair Face Blocks	Where walling is to be finished fairfaced, the blocks are to be selected free from defects.  Joints shall be raked out as works proceed and pointed with a neat flush joint.

The work shall be carried out regularly with all horizontal joints truly horizontal and no part shall be more than 900mm above adjacent work	during construction.

Sample Panel	The Contractor shall include in his tender for erecting a sample panel on site of 200mm blockwork, not less than 1 square metre in area and built off a suitable concrete foundation.  The sample, when approved, to form the standard for all concrete blockwork in the contract.  The sample area and concrete foundation to be removed when ordered and the surface of the ground made good.  Horizontal and vertical joints shall be10mm finished thickness, and raked out 12mm deep where face of wall is to be rendered and in other  cases to be left finished flush or as otherwise instructed.  The joint grooves between blocks shall be completely filled with cement, lime mortar.  No portion of the wall during construction to be more than 900mm above adjoining work.  All work to be executed truly level, perpendicular and properly bonded together without continuous upright joints.

Cement, sand and lime	Cement and aggregates for this trade except where separately specified for precise concrete blocks shall be as specified for “concretor” and lime shall be dry hydrated lime to B.S 890 Class B.

Air bricks			Form and leave neat holes in walls and supply and build in approved

loucred pattern concrete air bricks where shown.  The opening shall be rendered on all sides, the bottom sloped towards external face.

Bedding and pointing		Bedding and pointing of timber door and window frames shall be in

cement mortar.  Where frames are in metal they shall be bedded and

pointed in mastic.  Lugs or ties shall be built into walls as described.

Fixing blocks and	Provide and build into walls all necessary flying blocks and leave

and leaving holes	out or cut away as necessary holes for pipes, conduits and the like and make good after fixing by other trades and specialists.

Build in lugs and the like	Form or leave mortices in walls for, and build in lugs and all necessary fixing for metal windows and doors, door frames and lining, sanitary fittings, rainwater pipes, clips and bearer of various types.

- 4 -

When building up the walls the openings shall be made about 200mm wider than the external dimensions of the doors frames, and when the latter are placed, complete with lugs, the walling completed in concrete	mix type C.

Damp-proof course	Where indicated on drawings provide 2-ply felt damp-proof course.  Felt to be of a manufacture approved by the Architect and to be laid on a 25mm thick bed of cement mortar (1:3 mix) on walls.

The damp-proof courses to stand the full thickness of walls, partitions and  beams in one width and to be overlapped 6” at all jointings and corners.

Measurements	The Contractor must allow in his prices for block walling for plumbing angles, all straight waste, split courses necessary for bond, bonding at angles, intersections and juctions of walling at angles, intersections and juctions of walling of different thicknesses, cutting and fitting  to columns, cutting and pinning to beam, cutting and fitting around end of oils and lintols, cutting and pinning ends of structural timber.

The rates of blockwork must also include for fixing all door, window and like openings, forming reveals to same and for cutting and waste to walling in short lengths to millions and jamb of openings.

The rates of blockwork must also include for hoisting and building off beams and slab at any level, all necessary scaffolding and for work built overhead.

Mason

Cement and sand		Cement and sand for this trade shall be as specified for contractor.

Mortar for masonry work	Mortar for bedding and jointing of stonework shall comprise 1 part of cement to 3 parts of sand by volume.

Stonework in walls	All stones for use in walling shall be blue basalt stone carefully selected according to the type of walling required.  Walls to be built to the thick-ness shown  on the drawings and the stones wall be well bonded and all voids filled in solid with mortar, bond stones to be used on every 120mm vertically and 2700mm horizontally.

Mortar joints shall be raked to depth of 12mm from face of stonework ready for painting.  Walls exposed to sun shall be protected with sacking which  shall be kept thoroughly wet for at least three days or for such longer period of time as the Architect may direct.

Stone cladding works	All stones for use in claddings shall be Blue Basalts demolition stones carefully selected and to Architect’s approval. Claddings to be of the thickness shown on drawings and be well bonded with all voids sealed in solid cement mortar. All wall surface to receive proper cementious waterproofing prior to application of stone cladding and to be to Architect’s approval.

- 5 -

Pointing	All joints whall be raked out as described in Clause 3 and pointed with cement and sand (1:3) with approved pigment added.  The pointing will either be recessed, weather struck or flush.

Cleaning of stonework	The contractor shall protect the stonework from mortar droppings and wire brush and wash down all walls on completion.

Carpenter and Joinery

1. Timber generally	All timbers used in the works unless otherwise specified shall be one of	the following:

(a) For constructional work keruing, gurjun, mahogany or approved local  treated pine.

(b) For joinery work, mahogany, tekoma, teak

The timber shall be sound, selected, well seasoned vacuum impregnated With Tanalith Salts type C at the rate of 64 kgs per cu.m. of timber, free from all defects and shall be worked to the full sizes indicated on the	drawings.

In all cases samples of the timber for use in the building shall be

submitted to the Architect for approval prior to use.

2. Treatment of timber	The ends and backs of all doors, frames of all timbers built in, rosting or Indirect contact with walling or concrete where not exposed to view, shall be coated  with two coats of creosote, solignum or other approved preservative.

3. Replacement of	Should any of the timber warp, shrink, wind or fly to any apprciable

defective timber	extent within 6 months of completion of the works, the same shall be removed and new fixed in it s place at the contractor’s sole expense together with all other work that may be affected.

4. Preparation of		The preparation of the timber shall commence simultaneously with

timber	the beginning of the work generally and shall proceed continuously until the whole of the woodwork is prepared and stacked on the site, and properly protected from the weather.

5. Constructional		All constructional timber shall be properly jointed and framed

timber			together with dowels, bolts or spiked as indicated on the drawings.

6. Workmanship	All carpentry shall be executed with workmanship of the best quality.

All carpenter’s work shall be left with sawn surface except where

specified to be wrot.

- 6 –

All carpenter’s work shall be accurately set out and in strict accordance with the drawings and shall be framed together and securely fixed in the best possible manner with properly maderjoints.  Provide all brads, nails, screws.etc as  necessary and as directed and approved.

All timber shall be as long as possible and practicable, in order to

eliminate joints.

Actual dimensions of scantlings for carpentry shall not vary from the specified dimensions by more than 3 mm in deficiency or excess.

7. Protect floors	All timber bearded floors to be protected with sawdust after laying.  The sawdust to be cleared away on completion.

8. Joinery work		All joiner’s work generally to be cast and framed together as soon as

generally	is practicable after the commencement of the building, but shall not be wedged or glued until the building is ready for fixing same.

All work to be properly tenoned, shouldered, wedged, pinned, bradded etc. as directed by and to the satisfaction of the Architect and all properly glued up with best quality approved glue.

Oval or round brads or nails shall be used for fixing on face work, heads	properly punched in and the holes filled with putty or as otherwise described.

9. Finish to	All exposed faces of woodwork shall bet wrot, which shall mean bringing up the surface after planning with sand paper to a smooth satin-like finish.

10. Workmanship	All joinery work shall be executed with workmanship of the best quality in strict accordance with the detailed drawings.

All joiner’s work shall be accurately set out on boards to full size for

information and guidance of artisans before commencing the respective work.  All joints, ironwork and other work connected therewith fully declinated which said setting out will be required to be submitted to the Architect and approved before such respective works are commenced.

All mouldings shall be accurately and truly run and all work planned

and finished to the approval of the Architect.  All arises to be slightly rounded.

Should any of the joinery work shrink, warp, wind or develop other

defects within six months after the completion of the works, the same will be removed and now fixed in its place, together with all other work

which may be affected thereby, at the contractor’s cost and expense.

- 7 -

All plugs described as fixing for joinery etc. unless otherwise stated shall be formed by raw plastic Philplug screwfix or other approved patent material.  No woodplugs shall be used.

Any fixed jonery which in the opinion of the Architect is liable to

become bruised or damaged in any way shall be properly cased and

protected by the contractor until the completion of the works.

11. Door frames 		Door  frames and linings shall be constructed to the sizes and details

shown on the drawings.  Door frames shall be fitted with three fixing irons to each side of the frame and one at the head.  Frames for double doors shall have two fixing at the head.  The fixing irons shall consist of 300mm long heep iron not less than 3 mm thick  bent up 75mm at one end and twice screwed  to the frame and the other end built into walls or cast into the lintols to a depth of 225mm (where lintols are less than 225mm deep the straps shall be cut off to the full depth of the lintol). 6mm diameter metal dowels shall be fixed to each end of the frame and let into the floor concrete to a depth of at least 50mm. Door linings shall be screwed to wooden fixing slips let into the walls And lintols.

12. Doors	Doors shall be provided and fixed to the sizes and details shown on the drawings.  Doors shall be free from all blemishes and shall be rubbed down to a satin-like finish.  Frames, ledged and braced or ledged and braced doors shall be made to the sizes shown on the drawings and the nailing in construction shall be driven from the face and clenched at the back.  The heads of nails shall be punched and the holes filled with petty.

The flush doors are to be equal in all respects to the samples of each type to be submitted to the Architect for approval.  The coves of all doors shall be pressure bonded and stacked for inspection before the faces are fixed.  The plywood facings shall be of the same species on both sides of each door unless otherwise stated.

Facings shall be free from lifting at edges, blisterings or sinking or

raising of the surface due to defects in the base of materials.

13. Hardboard	Hardboard shown on drawings for linings, ceilings and joinery shall be of approved manufacture.

14. Veneered plywood	All veneered plywood or blockboard is to be counter-veneered on the reverse side.  Plastic faced material shall also be counter-veneered if and where necessary.

- 8 -

15. Formica	Formica shall be as supplied by Messrs Formica Ltd.  De la Rue House,	84 Regent Street, London W.I.,  England or similar approved, of approved colour and pattern and fixed with an approved adhesive in accordance with the manufacturer’s instructions.

16. Ironmongery	Butts and hinger shall be of sizes and types specified and fixed with the full number of screws and on no account shall nails be used.

All locks and ironmongery shall be fixed before the woodwork or metal work is painted.  Handles shall be removed carefully stored and re-fixed after the completion of painting.  Locks shall be oiled and left in perfect working order.  All locks to include two keys and all keys shall be labelled with door references marked on plastic labels before handing to the Architect on completion.

17. Plugging and		Where items are described as plugged or plugged and screwed this

screwing	shall mean plugging, plugging and screwing to concrete  blockwalling, concrete walling, stone walling to the approval of the Architect.

18. Prices of			The Contractor is to include in his prices of all members for fitted

timber work	ends,nitres, housings, returned ends, etc. and for short-lengths not exceeding 300mm.

The prices for all joinery items are to include for slightly rounding all arises and extra cost of labours crossgrain.

Where hardwood is described as screwed, prices are to include for

pollating with a natching hardwood.

Allowance is to be made in the prices for angles, ramps, nitres, ends, etc.on timber  worked on solid and shall include for all necessary non-ferrous metal screws.

The prices for all timber described as select quality are to allow for

keeping clean for light coloured finishes, polishings, etc.

Ironmonger, stitch and metalworker

1. Ironmongery		All ironmongery and furniture to be approved by the Architect as to

quality and type and locks to be fixed to the correct hand.

2. Oiling of			All locks, ironmongery and hinges including the moving parts of

locks, etc.	metal doors and windows to be well oiled, and all necessary adjustment made before  handing over the works.

3. Metal windows		All metal windows and doors shall be hot dipped galvanized after

and doors 	manufacture and shall be from a manufacturer approved by the Architect.

- 9 -

They shall be  of  sizes and types shown on the drawings and shall be ordered by the Contractor and windows shall have bronze fittings with projecting hinges unless otherwise specified complete with building in lugs and glazing pins.  Metal doors and windows bent or damaged during construction of the building shall be replaced at the contractor’s expense.

4. Cyclone bolts	All openings sashes of metal windows shall be fitted with two cyclone bolts consisting of an extruded brass case with stamped brass sheet 115mm long complete with socket or wedge,

5. Louvre windows	Louvre frames to be anodized aluminium with clips of the size specified suitable for taking 6mm thick glass blades screwed to concrete jambs with 38mm screws.

Mullions to be formed by coupling 56mm x 6mm thick anodized

Aluminium mullion strips bolted through to the box mullions, and fix to lintol and cill by means of retaining brackets screwed to rawplugs in concrete with No. 4  38mm screws.

Weather strips to be in anodized aluminium and to be screwed to

rawlplugs in concrete at head and cill with 38mm screws.

Workmanship			Workmanship and materials shall be of the best quality.

Prices of all doors, windows and louvers shall also include for all

necessary cutting and pinning, plugging and screwing to concrete or

block openings and for making good of finishes.

Pavior

1. Cement, sand		Cement, sand and aggregates for this trade shall be as specified for

and aggregate		“concretor”.

Coral sand shall have three washings.

2. Preparation of		The surface of the concrete shall be hacked to form a good key, well

surface to receive		washed and brushed perfectly clean with a wire brush to remove all

screedings and		impurities,  dust etc damped and grouted with a mixture of cement

pavings	and water in the form of slurry, using 2.75 kgs of cement per sq.m. of surface area, before screeds are laid.

3. Plain screeded		Floors to have plain screeded finish shall be laid in areas not

pavings	exceeding 10 sq.m at one time using teak 6mm x 19mm stop fillets.  Screeds to be	minimum of 19mm and to be composed of one part of cement to 3 parts of sand.  The surface to be finished to a polished surface with a steel trowel.  The screeds or pavings shall be kept wet with sand, sacking or similar for at least seven days after completion.

- 10 -

4. Coloured			Coloured screedings shall be laid in a similar manner as for plain

screeded pavings	screeding with addition of approved liquid colouring mixed in with the mortar strictly in accordance with the manufacturer’s directions and to approved shade, and kept wet for seven days after completion.

5. Expansion joints		At the entrance of each room directly under the door, fix a teak strip

6mm x 19mm deep for full width of opening to form an expansion joint between adjoining screeds.

6. Granolithic			Shall be laid in areas not greater than 10 sq.m. at one time using

paving	teak 6mm x 19 mm fillets.  Granolithic paving shall be composed of two parts by volume of cement to five of blue basalt  chippings to pass a 6mm square mesh free from dust and containing not more than 10% grit.

Granalothic paving to be well watered and kept damp for seven days

after laying.

7. Polishing of			When laid the Granolithic paving shall be rubbed down with a

granolithic pavings		carborun-dum stone to give polished surface.

8. Non-slip surfaces		Surfaces of internal pavings and steps where required to be made

to pavings	non-slippery shall be created with coarse carborundum average 11.4 kgs per m2   lightly trowelled in while the paving is still green.

Surfaces of external pavings or steps where required to be made non

slippery shall have parallel lines 12mm deep and 9mm wide in the

surfaces of the paving or concrete.

9. Quarry tiling	Quarry tiles shall be to the quality, sizes and colour as selected by the Architect, laid to areas indicated on the drawings.  The tiles shall be set square jointed bedded and pointed in cement mortar (1 part of cement to 3 parts of sand).

Tiles shall be soaked in water 24 hours before laying and shall be

thoroughly scrubbed to remove all traces of cement after laying and

protected with sawdust or sacking and not used for at least 10 to 14 days.

The surface shall be polished on completion of the contact.

10.Polishing paved		Types of floors described in clauses 4 and 7 shall be cleaned on

surfaces	completion of the works and treated with two coats of floor polish each coat rubbed well in and polished.

11. Roof screed	Roof slabs shall be finished with a cement/sand screed 1:3 mix laid to falls and crossfalls and minimum thickness 19mm. unless specified other-wise in bill of quantities to which shall be added an approved water-proofing liquid used in strict accordance with the manufacturers’ written instructions.  Screeds shall be carried down rainwater outlets and finished

neatly against the downpipe. The screed shall be kept wet for at least

seven days after completion

- 11 –

12. Prices of pavings		Prices for pavings or screeds are to include for preparation of the

and screeds tiles etc.	concrete base, all necessary hacking, grouting with cement grout, any extra thickness consequent upon the concrete surfaces not being finished to true and level, laying in bays and all necessary formwork and dividing strips and cutting the finished screed or paving for at least seven days.

Prices for tiling shall also include for all straight and raking cutting, fair edges and fair joint, prices for tile skirtings shall further include for angles, ends, nitres and for short lengths not exceeding 300mm.

Plasterer and wall tiler

Generally	The renderings are to be carried out so that the finished surfaces appear 	Without visible joints or patches.  The rendering of wall surfaces, reveals of openings and cills are to be carried out in one operation and each day’s work stopped at a suitable point where it can be picked up again on the following day without noticeable joints.  The quality and mixing of the materials are to be constant throughout so that there is no variation in colour or texture.  The finished coat to be brushed down and left clean to be received decoration.  In  any continuous face of a wall the rendering

shall be carried out continuously and day to day breaks made to coincide with architectural breaks in order to avoid unslightly junctions.

Preparation of			All  faces of concrete work shall be well hacked to form a good key

surfaces for rendering	and in the case of block or stone walls the joints shall be raked out.  All surfaces for rendering shall be well wetted with a hose before rendering is applied

Cement			Cement shall be as specified in “concretor”.

Sand				Sand shall be as specified in Fine Aggregates in “Concretor” but in

Addition shall be in accordance with B.S. 1199 and shall if CORAL

SAND have three washings in lieu of 2 for internal work.

Lime				Lime shall be either in the form of quick lime and obtained from an

approved source and properly stacked on site or in the form of dry

hydrated lime and conform to the requirements of B.S 890 Class B

“Quick lime or Hydrated Lime for Corse Stuff and Building Mortar”.

Rendering			The mix for rendering both internally and externally shall be 1 part

of Cement to 1 part of lime to 5 parts of sand plus an approved mortar	plasticizer used strictly in accordance with the manufacturers’ written instructions.

Application of			All external surfaces shall be rendered in two coats unless otherwise

Rendering			instructed.

- 12 -

The first coat of rendering shall be applied with wooden float to an even thickness of not less than 10mm and not more than 15mm.  As soon as the first coat starts to set it shall be closely combed to a depth of 3mm to 6mm and kept damp for at least two days after which time the final coat

shall be two days after which time the final coat shall be applied to an even thickness  of not less than 6mm and not more than 25mm.

All rendered  surfaces shall be kept damp for at least two days after the final coat has been applied.

Finishes to			Rendered surfaces shall be finished as directed by the Architect in

renderings			the following manner:

(a) Wood floor finish:  Finish surfaces with a wood float to an even and slightly/rough textured finish.

(b) Sponge finish:  Finish rendered surfaces with a steel trowel and while the rendering is still green dab the surfaces with a damp sponge until they present  a fairly sanded textured finish.

© Trowel finish:  Finish rendered surfaces with a steel trowel to a smooth and even surface, free from trowel marks.

Tyrolean Finish	Tyrolean rendering shall consist of a 12mm backing coat of one part of cement  with 10% of lime by volume added to four parts of sand,

trowelled up to a true surface left as open as possible (no combing or scratching required) followed by a tyrolean finishing coat of white cement (snowcrete or other equal, and sand of a suitable mix applied with a spraying machine and built up in three coats to a total thickness of 8mm approximately to the approval of the Architect.

Sample panel	The  Contractor shall prepare samples of plastering tyrolean  finish, bush-hammered finish as directed until the quality texture and finish required is obtained and approved by the Architect, after which all plastering, tyrolean and bush hammered finish expected in the work shall conform to the respective approved samples.

Arrises				Vertical and horizontal arrises  shall be formed to beams, columns,

openings and the like and shall be pencil rounded.  Particular care shall be taken to ensure that the rendering is strong and sound at the corners.

Cracks, blisters, etc	The Contractor shall make good all cracks, blisters and other defects and leave the whole of the plaster, tyrolean, bush-hammered finish perfect at completion.  When making good defects the plaster shall be cut out to a 	rectangular shape with edges undercut to form dove-fitted key and all finish flush with face of surrounding plaster all at the contractor’s own expense.

- 13 –

Plinths				Form plinths is external rendering as shown on drawings.

Wall tiling			Wall tiling unless otherwise stated shall be of glazed earthenware

tiles of The dimensions and colours specified and shall conform to B.S 1281 and shall be of approved manufacture true to shape and free from blemishes.

The backing coat for wall tiling shall be in cement: sand mortar (1:2

dx),not less than 9mm  and not more than 15mm thick, the surface of which shall be closely combed while the mortar is still green and left for a period of 24 hours.

The tiles shall be soaked in water for 30 minutes and bedded with an

Adhesive of the approved manufacture.

All tiles shall be laid perfectly level, the joints to run straight horizontally And vertically and to be pointed in neat cement to an approved colour.

Internal and external angles and rounded edges tiles are to be of the same manufacture,  colour and thickness as the foregoing.

Prices of plasters,	Prices of plastering are to include for preparation of the surface, hacking of concrete, raking out joints of blockwork, grouting, forming temporary rules, fair edges and arrises, rounded external angles, vee joints, working to rebates making good to window or door frames, around pipes, holder- bats,  sanitary fittings, narrow widths and small quantities.

Prices for rendering on walls shall also include for any extra labour

involved in working to breaking columns, beams, cills, etc, all of which have been included in the general term of walls.

Prices for wall tiling shall include for all operations required in proper	execution of the work out and waste and fixing as described.

Glazier

Quality of glass	All the glass to be of the best quality obtained free from all defects and Imperfections and shall be to the approval of the Architect.

Windows and doors	Glaze all windows and doors in minimum 6 mm thick laminated glass unless specified otherwise.

Translucent glass	Windows requiring obscure vision shall be glazed with translucent glass of an approved texture or pattern, the thickness to be not less than that mentioned above unless specified otherwise.

Putty	Putty for glazing to wood shall be made of pure whiting and raw linseed	oil and to be used fresh.  Putty for glazing to metal shall be steel sash putty of approved manufacture.

- 14 -

All putty shall be delivered on site in the original manufacturer’s sealed cans  or drums and used direct therefrom, with the addition only of pure linseed oil if necessary.  No mineral or other cils shall be used in the	putties except genuine linseed oil.

The rebates of metal window shall be painted one coat before puttying.

Glazing	All glass to be cut accurately in one piece, to fit easily into their rebates and to  be well puttied, back puttied and secured with springs in the case of fixing to wood or with metal clips in the case of metal.  Care must be taken to ensure that the putty does not show beyond the sight lines of panes and that the putty is neatly cut off internally and neatly splayed off externally all mitres and angles left clear and sharp.

Glass blades for	window		Blades for louvre windows shall be laminated  6mm thick glass of louvre 					selected glazing quality Grade ‘A’ to B.S 952 and of approved 						manufacture.

Fire resistant glass		Fire resistant glass to be fire resisting glazing of 60 mins integrity 						meeting BS 476:part 22.Each glass sheet to be provided with a visible 						“acid etching” giving the trade name in the corner of the pane and mark 					with BS 476:part 22.Fire resistant certificate to be produce at approval 						stage,

The two long edges of  the blades shall be flat smooth polished with no

sharp arrises and the two others clean cut.  The contractor shall, when

requested  to do so, produce certificates of proof of manufacture and

quality of the glass blades he proposes to use.

Glazing work at			All glass broken, cracked or scratched during the progress of the works to

completion			be reinstated at the sole cost of the contractor and all glazing to be left

clean and perfect at the completion of the contract.

Painter & Decorator

Generally			All work shall be carried out in strict accordance with schedule of

colours to be obtained from the Architect.

Samples of colours if requested by the Architect shall be painted on the

walls 1.00m x 1.00m square and approval obtained from the  Architect

before proceeding with the work.

Materials, paint,			All oil paints, emulsion paints, varnish and other materials shall be of an

Varnishes, etc			approved  manufacture and shall be used strictly in accordance  with the

manufacturers’ printed instructions, the contractor will only be allowed to

use materials which are brought to the site in sealed cans not exceeding

one gallon capacity, bearing the name of the manufacturer and properly

labelled as to quality.  Exterior quality paints only shall be used, both

internally and externally.  All cans of paint must be kept well stirred

before and  during use.  The only addition to the paint which will be

allowed shall be approved pure turpentine and this shall be added only in

accordance with the Architect’s instructions.  All coats of paint applied

over each other shall be from the same manufacture and the type

recommended by the manufacturers

- 15 –

Well before commencing the painting work the contractor shall submit to the Architect for approval a list of all the brands of paint and finishings including the necessary primers and undercoats he intends to use and immediately upon being so approved orders shall be placed and total requirements obtained for the works.

Once approved no other brand of materials shall be used without the

express permission of the Architect in writing.

Preparation of 			All surfaces to be painted shall be thoroughly cleaned down and

Surfaces	surfaces of wood to be sand-papered and to be twice knotted and stopped before applying the priming coat which shall be regarded as additional to the undercoat.  All surfaces of  ironwork to be thoroughly cleaned  of all scale, and every particle of rust, dirt or grease removed by scrapers’ and wire brushes, or other approved method.  Galvanized, sheradised or zinc sprayed metal to be painted shall be treated with mordant solution.

Copper pipes specified to be painted shall be rubbed down with coarse emery, cleaned with a solution of one part acetone to two parts of benzel and left to dry.

Wood				Treat all timber  built in or in contact with walling and concrete with

Preservative			2 coats of approved type of wood preservative.

Galvanised metal		Clean down, treat with degreasing solution, prime with yellow

Surfaces	chromate or other approved primer, and paint two undercoats and one gloss finishing  coat oil paint.

Ironwork			Clean down, removing every trace of rust and paint 1 coat of red

lead primer, 2 coats of undercoat and one gloss finishing coat.

Rendered surfaces		Brush down to remove dirt and dust, prime with alkali resistant

primer as specified by the suppliers of the emulsion paint to be used

and paint three coats of approved plastic emulsion paint (external

quality) both internally and externally strictly in accordance with’

manufacturers instructions.  The walls are not  to be  pumiced down.

Cleaning on			All floors to be twice washed, all marks of paint to be sponged off,

completion	windows cleaned, the work  generally to be touched up after all the other trades are finished and the whole of the building left clean and perfect on completion to the satisfaction of the Architect.

Laboratory furniture		All laboratory furniture are to be finished with one coat

and wall cupboard, 		polyurethane lacquer of approved manufacturer.  The first coat is to

workbench			be gloss lacquer thinned with 10% white spirit and applied to all

surfaces including the back of fittings, inside of drawers, and doors, etc.  All exposed surfaces are to be finished with a further cost of semi-gloss lacquer.  Hardwood bench tops are to be finished with two coats or linseed oil.

- 16 -

Plumber

General			All materials and workmanship shall comply with the latest editions

of The British Standards’s  Specification, Codes of Practice, By

Laws and Regulations of all Statutory Authorities concerned.

The Contractor shall include for producing all working drawings,

details,builder’s work and holes drawings necessary to carry out the

work and as required by the Architect.  The drawings shall be based

upon the Architects  diagrammatic drawings and shall be submitted, in duplicate progressively at least two months prior to the programmed commence-ment of work coordination and approval of the Architect.  All alterations	to drawings, whether due to co-ordinations or otherwise, shall be carried out by the contractor.  The contractor shall provide the Architect with four copies of each approved drawings in addition to those required for his own use.

At completions of the contract, the Contractor shall provide the

Architect With one complete set of negatives  indicating the “As installed”  installation and three prints of the said drawings complete with all operational  and maintenance instructions, value charts, and test certificates.  These drawings  shall be provided to the Architect at practical completion of the works, failing which the Architect reserves the right to withhold an appropriate portion of the first retention money.

All work shall be tested in sections as required and before being covered up, for the Architect and statutory authorities.  Before any test is carried out, a minimum of seven days notice shall be given to the Architect.

Where access is indicated to soil, waste and rainwater pipe fittings, the Contractor shall ensure that all access doors and rodding eyes are so positioned as to be accessible.  Before testing, all access doors shall be removed, inspected, the washer greased and then reassembled by the Contractor.

Lead in  flats			The lead used shall be best milled sheet lead of  approved

flashings,  aprons etc.	manufacture. No solder to be used in laying of lead except where quite unavoidable and no continuous strip of lead to be more than 2.00m long.  Overlaps to be not less than 75mm.  Lead flashings, aprons, soakers and other lead work where required to be fixed shall be secured  with copper nails.

Leadwork shall comply with the following weights.

Per sq.ft

Lead gutters & flats				29.3 kgs

Flashings and aprons				24.4 kgs

Soakers					19.5 kgs

- 17 -

Soil ventilating		Soil ventilating pipes shall be not less than 63mm interval diameter

pipes				cast iron pipes conforming to B.S.S and fitted with the necessary

junctions and bends.  All joints shall be made with a gasket of tarred hemp and caulked with a mixture of neat cement just moist.  The pipes shall be secured to the wall with approved holderbats which shall be securely fixed to the wall with rawlbolts.

Ventilating pipes shall be carried at least 900mm above eaves level and shall be fitted with approved coated wire balloon.

Rising Main	The Contractor shall include for all charges for tapping and connection to public water main, including all necessary excavations and reinstatement of public roads.

Galvanised pipes and		All internal and external water services, fittings, wastes, overflows

fittings for water		and the like shall be in screwed and socketted galvanized wrought

services			iron or steel tubes and tubulars, the former complying with BS 788

for water (medium) and the latter with BS 1387 for B class.  Pipes

above ground level shall be fixed to walls with approved type

galvanised malleable iron built in clips, brackets, holderbats or pipe

clips, the spacing of which shall not exceed 900mm.

The jointing of galvanized piping and fittings shall be made with

proprietary brands of jointing paste or compound complying with BS 1260 and if these are not obtainable by a method to be approved by the Architect.

Unless otherwise specified or detailed on drawings the internal diameter of service pipes shall comply with the following:

Diameter of supply						No. of tappings shall

or feed pipe							not exceed

13mm								2-13mm

19mm								4-13mm

25mm								  -13mm or 2 – 19mm

31mm								10-13 mm or 2 – 25mm

38mm								16-13mm or 6 – 19mm

3 – 25mm or 2 – 31mm

Water taps	All bib, pillar, globe and stop taps shall be of the screw down

pattern and comply in every respect with BS 1010.  The size

specified or shown on the drawing shall mean the maximum bore

of the seating.

Stopcocks and boxes	Brass stopcocks shall be provided at the immediate entry of the

water services into the building and at the other points as

indicated on the drawings and shall be of a pattern approved by

the Architect.

- 18 -

Stopcock boxes where required externally shall be constructed of

150mm earthernware pipe out to the required length and fixed

vertically over the stopcock on two concrete blocks and the earth

well consolidated round the sides.  Top of pipe to be fitted with

225mm x 25mm, thick precast concrete cover reinforced with

13mm  chicken wirenetting and fitted with a lifting ring.

Testing of water		The whole of the water services laid or fixed by the

services	 		contractor shall be tested at the contractor’s expense in the presence

of the Architect and shall comply with his requirements and any

defects made good to his satisfaction.  In the absence of instructions

regarding the test it shall be an air pump and pressure gauge test

the pressure applied at 35 to 53 grms per cm2  for one hour at the

end of which period the loss in pressure shall not be greater than

1/50th of lb. per 225 mm2.

Waste pipes			Waste from sinks and shower to be in 38mm bore pipe and from

lavatory basins to be 31mm.  All wastes to be carried through

external walls to discharge over gulley gratings.  All wastes pipes

shall be at each change of direction of pipe be fitted with a tee,

one end with screwed plug for cleaning purposes.  The  external

gulley to be connected to the nearest manhole.  Wastes from

urinals to be taken in 50mm diameter cast iron pipe with trap at

urinal end and connected by 50mm pipe externally to the nearest

manhole.  All laid to fall.

Overflow pipes		Overflow pipes are to be fitted to all w.c  distant tanks and baths

and in each case the overflow pipe shall be 6mm longer in

diameter than the water supply to the unit.  Overflow pipes to w.c

cisterns shall be taken through an external wall to finish 150mm

beyond the face of the wall.

Supply of sanitary		Baths, w.cs, basins, sinks and other sanitary units shall be of

ware				approved manufacture and shall comply with the relevant B.S.S.

They shall be of the type and designs shown on the drawings or to

the Architect’s instructions.  The whole  of the units shall be

properly fixed and connected to the water service complete with

wastes and overflows as described.

Rainwater pipes		Rainwater pipes shall be approved rigid P.V.C rainwater unless

otherwise described.  Pipes shall be properly fixed to walls with

approved clips at distance to be directed by the Architect.

Drain pipes for		All pipes for soil drainage which include the conveyance of

soil drainage			discharges from wcs, basins, sinks,  drains, baths and showers

shall salt-glazed earthernware pipes, bends, junctions and tapers

complying in all respects with B.S no. 63 for “British Standar

- 19 –

Pipes” and must be stencilled with the registered mark of the

B.S.I.  Other fittings shall comply with the dimensions laid down

in B.S 539.  If the above type of pipe is unobtainable then best

Commercial Quality may be used on conditions prior approval of

the Architect is obtained.

Drain pipes for 		Pipes conveying storm or surface water shall be second quality

water drainage			distinguished by a black band.

Laying of drain pipes		The pipes  to be laid in straight runs to even and regular falls, and

put together with great care, the spigot of one pipe shall have one

lap of tarred gaskin wrapped round it and then placed into the

socket of the pipe previously laid.  After the adjustment the

gaskin shall be caulked lightly home but not so as to occupy more

than one quarter of the socket depth.  The socket shall then be

completely  filled with cement mortar (1:1) and a fillet shall be

formed round the joint, with a trowel forming an angle of 45

degrees with the barrel of the pipe.  The joint inside to be struck

with a scraper, so as to give a perfectly clear and unobstructed

water way.

Fall in drains			All pipes except where otherwise shown shall be 125mm internal

diameter laid to a fall of 1:50.

Concrete bed to drains	Concrete (1:3:6) shall be laid 150mm thick to form bed for drains

where the soil is found to be soft.  After the pipes have been

tested, it shall be haunched up on both sides  to a height of 3/4th of

the internal diameter of the pipe.

Concrete cover to drains	All pipes passing under buildings or under roadways shall, in

addition  to a 150mm concrete bed under, be completely

surrounded in concrete of the same thickness of (1:3:6 mix).

Gully traps			Provide trapped gullies, complete with gratings in positions

shown on drawings, set on concrete and surrounded in concrete,

and jointed to drain as described.

Manholes			Manholes are to be constructed in the positions shown on the

drawings.  The internal dimensions of the manholes shall vary

according to their depth and shall be as follows:

Depth of manhole from 					Internal dimensions of

top of invert to finished					manhole shall not be less then

ground level

Up to 600mm							600 x 450mm

Up to 900 mm							750 x 600mm

Up to 1200 mm						825 x 675mm

Up to 1500mm						900 x 750m

- 20 –

Exceeding 150mm in depth the Contractor shall apply to the Architect for details.

Manholes shall be constructed in concrete (1:3:6) cast in situ hacked for key and finished above the benching with 6mm thick rendering of cement and sand mixed in the proportions of 1 to 2.  The thickness of the concrete walls shall vary according to the depth and shall be as follows:

Depth of manhole from				thickness of concrete to

top of invert to finished				manhole walls shall not be less than

Up to 600mm deep					100mm thick

Exceeding 600mm but not				150mm thick

Exceeding 1500mm

Exceeding 1500mm in depth the Contractor shall apply to the Architect for details.

The floor of manholes shall be 150mm thick and the channels and benching   shall be formed above the level of the floor in fine concrete (1:2:4) average 225mm thick with a polished fall and carried up 450mm above invert level and channels.  The cement for benching to be sulphate resisting cement.  Step  irons shall comply with B.S 1247 and shall be placed at intervals of 450mm vertically with 300mm offset between alternate steps.

Manhole covers other than those in roadways shall be 600 x 450mm cast iron medium weight with frame set flush in 125mm concrete cover slab Mix C,, the building shall be bedded in grease and shall be of an approved heavy iron pattern and the contractor shall apply to the Architect for details including the construction of the manhole.

Soakaways			Construct soakaways not less than 6m away from the building in

position approved  by the Architect.  Water from rainwater pipes

to be first taken into a trapped gulley below rainwater pipes to be

first taken into a trapped gulley below rainwater pipes and thence

by 100mm diameter pipe to soakaway.  The soakaway to be

900mm x 900mm x 1500mm deep filled with stones and finished

with a 300mm layer of 38mm macadam.

Cast concrete kerb around gulley and soakaway in mix B concrete

100mm thick and 225mm deep to project 125mm above ground

level.  Render kerbs with a 1:3 cement and sand and finish with

slightly  rounded edges.

Septic tank			Septic tanks shall be constructed in position shown on the site

plan not less than 15m. away from the building, in accordance

with  detail drawing.

Intercepting chamber		Intercepting chamber shall be constructed as described for man-

holes with an approved saltglazed eathernware intercepting trap

with rodding arm fitted with standard jointed stopper set and

surrounded in concrete mix C and jointed to drain.

- 21 -

Fresh air inlet			Build into the side of the intercepting chamber a 100mm diameter

cast iron pipe with bend to terminate not less than 750mm above

ground level jointed to an approved 100mm galvanized fresh air

inlet valve with cast brass flap and hinged mica flap.

Drain testing			All drainage runs shall be tested before tracks are filled up and

afterwards when the drainage system is complete in the presence

of the Architect.  The contractor shall supply all necessary

equipment and labour for carrying out the tests.  The air test shall

be carried out by plugging all openings with standard air test

apparatus to one end.  The air pressure in pipes to be built up by

means of a suitable pump until a head of 100mm is reached and

the test continued until approved by the Architect.  The maximum

loss allowed shall be a fall of 25mm over a period of 5 minutes

after pumping has ceased.  If the fall exceeds 25mm a smoke test

shall be immediately carried out to locate defects and all such

defects shall be made good and further tests carried out at no extra

cost to  the Employer.

ROADS AND FOOTPATHS

Site clearance			All roots, tree stumps, rocks and similar obstructions in the line of

The excavation of the road or footpath shall be removed from the

site having due regard to Clause No. 1 of the Excavator section of

this specification.

Macadam finished roads	Excavate to a depth of 225mm below the required finished level

of the road, and to the full width directed.  All excavated

materials shall be spread and levelled on the site or removed from

the site as directed by the Architect.

Tarmacadam roads,		Remove top soil to a minimum depth of 225mm and compact

Drives playground, etc.	formation level by a 8-10 ton roller.  Where formation is

composed of clayed soil (to be decided by the Architect) apply a

Operation 1			layer of coral sand 38mm thick and compact again.

Operation 2			Hardcore filling consisting of angular shapes blue basalt spalls

150mm x 100mm x 75mm type B to be placed on the compacted

surface after operation 1, blinded with 63mm aggregate and

compacted with the 8-10 ton roller by successive passes until a

well  interlocked mass is obtained.

Operation 3			Spread 25mm aggregate on the compacted hardcore filling after

operation 2 at the rate of 16-18 sq. metre of surface per cu.metre,

blinded with 19mm aggregate at the rate of 40-50 sq.metre of

surface per cu.metre and compacted with the 8-10 ton roller until

no movement of the 19mm aggregate is possible.

- 22 -

Operation 4			Spray bitumen of 6/70 penetration at a temperature of 300ºF

(using a bitumen sprayer) at the rate of 2 sq.metre per gallon,

followed immediately by 9mm aggregate at the rate of 150 sq.

metre of surface per cu.metre and  rock sand at the rate of 300 sq.

metre of surface per cu. metre compact with a 8-10 ton roller after

the surface has been smoothed up by hand and brass brooms.

NOTE:  The surface to be finished to the level decided by the

Architect on site.

Kerbing in stone		Edges of all roads requiring stone edging; the level kerbing shall

be made of selected rocks with level and square exposed edges of

full thickness of the hardcore and finished flush with the road

surface.

Kerbing in concrete		To edges of all playground and paved areas except where other-

wise indicated provide 300mm wide and 225mm deep concrete

curbs, cast in situ to full widths and depths of 1:2:4 concrete, with

smooth trowel finish to exposed edges and finished flush with and

to follow falls of paved areas.  At inter-sections of curbs and at

intervals of 30 metres in straight run provide 13mm wide butt

jointed expansion rail to back of kerbs to within 50mm of top of

curb and where filled filling to be banked at a slope not exceeding

1 in 3.

EXCAVATION

2.1  Inspection of Site

The Contractor is deemed to have visited the Site and to have ascertained the nature of the material to be excavated.

2.2 Dealing with water

The contractor’s attention is drawn to the depths below ground level of the foundations and the consequent possibility of having to deal with water.  Unless otherwise specified the contractor will be required by pumping or other means to keep the exactions dry during construction.

Shoring of existing structure

The contractor’s attention is drawn to the requirements for shoring  parts of the structure of the existing building during construction and the consequent need to carry out the excavation in stages.  He is not allowed to excavate within the proximity of the existing structure without the drawings and/or instructions by the Engineer to do so.

- 23 -

  - Excavation Dimensions:

The excavation are to be executed to the widths and depths shown on the Drawings or to greater depths if instructed by the Engineer to obtain satisfactory foundations.

If the contractor excavates to any widths or depths greater than those shown on the Drawings, or as instructed by the Engineer he shall at his own expense fill in such widths or depths beyond that instructed or shown with concrete Grade “D” to the satisfaction of the Engineer.

  - Rock

“Rock” means any hard material, which in the opinion of the Engineer can be removed only by use of compressors or by wedging and the Engineer’s opinion shall be final.  Decomposed rock, tuff or other material which can be removed by pick, traxcavator or other mechanical plant will not be classed as rock.  All material classified as rock may, if approved  by the Engineer, be used as hardcore filling and the measured quantities of imported filling will be adjusted accordingly.  All rock so used must be broken to the required size as hereafter described before being used.

  - Blasting:

No blasting will be permitted.

  - Bottom of excavations to receive foundations:

The Contractor shall report to the engineer when secure bottoms to the excavations have been obtained.  Any concrete or other work executed before the excavations have been inspected and approved, shall if so directed, be removed and now work substituted after the excavations have been approved, all at the Contractor’s expense.  The surface of the bottoms to excavations shall be levelled or graded to falls as required, with 50mm layer of concrete Grade “D” blinding (maximum 20mm gauge aggregate) and finished to a smooth surface with a wood float.

  - Hardcore filling:

Hardcore for filling under float, etc, shall be good hard stone ballast to the approval of the Engineer, broken to pass not greater than a 150mm  ring or to be 75% of the finished thickness of the layers being

completed whichever  is the lesser and graded so that it can be easily and thoroughly compacted by rolling.

The filling is to be laid in layers each of a consolidated thickness not exceeding 225mm and well watered and rolled  with a vibrating roller (minimum 14 tons) or a ten ton roller.  Where rollings impossible, compaction shall be  by hard or mechanical tampers.  The top surface of the  hardcore shall be levelled or graded to falls as required  and blinded with similar material broken to 25mm gauge and surfaced  with a 25mm layer of stone dust, well  watered and rolled to receive concrete as described.

  - Materials found in excavations

No material found in the excavation is to be used in the works without the written permission of the Engineer

- 24-

CONCRETE  WORK

  - Architect/Engineer

For the purpose of the concrete structure the Structural Engineer shall be deemed invested with the duties and be the representative of the Architect.

  - Code of Practice

All workmanship, materials, tests and performance in connection with the reinforced concrete work shall be in conformity with the latest edition of the British Standard Code of Practice (C.P. 110 “The Structural use of Concrete”) where not inconsistent with these Preambles.

  - Supervision

A competent person approved by the Engineer shall be employed by the Contractor whose duty will be to supervise all excavation operations, making and erection of formwork, sending and fixing of reinforcement and all stages in the preparation and placing of the concrete.  All cubes shall be made and side test carried out under his direct supervision, in consultation with the Engineer.

  - Contractor’s  plant  equipment and construction procedures:

Not less than 30 days prior to the installation of the contractor’s plant and equipment for processing, handling, transporting, storing and  proportioning ingredients and for mixing, transporting and placing of concrete, the contractor shall submit drawings for approval by the Engineer, showing the proposed general plant arrangement, together with a general description of the equipment he proposes to use.

After completion of the installations, the operation of the plant and equipment shall be subject to the  approval of the Engineer.

Where these Preambles, the Bills of Quantities or the Drawings require specific procedures to the followed, such requirements are not to be construed as prohibiting the use by the Contractor of alternative procedures if it can be demonstrated to the satisfaction of Engineer, that equal results will be obtained by the use of such alternatives.

Approval of plant and equipment or their operation, or of any construction procedure, shall not operate to waive or modify any provisions or requirements contained in these preambles governing the quality of the materials or of the finished work.

  - Levels and Foundations:

The foundations of the works shall be carried down to depths as may be directed by the Engineer and they must be cut as nearly to the size of the concrete as possible and the vacant spaces between the concrete  and the solid ground, excepting where otherwise shown, must be carefully filled in as instructed by the Engineer.

All temporary timbering shall be removed but should any timber be left in or should any other work be done beyond that specified, it will be at the Contractor’s own cost.

- 25 -

  - Tolerances:

On all setting out dimensions of 7.5m and over a maximum non-cumulative tolerance of plus  or 6mm will be allowed, and for those under 6m  the allowable maximum non-cumulative  tolerance will be plus or minus 3mm.  On the cross sectional dimensions of structural members, unless otherwise required by the Drawings, a maximum tolerance of plus or minus 3mm will be permitted.

The top surface of concrete floor slabs and beams shall be within 6mm of the normal level and line shown on the Drawings.  Walls and columns shall be truly plumb and non-cumulative tolerance of 3mmin each storey and not more than 12mm out of plumb in their full height will be permitted.  The contractor shall be responsible for the cost of all corrective measures required by the Engineer to rectify work which is not constructed within the tolerances set out above.

  - Materials generally:

All materials which have been damaged, contaminated or have deteriorated or do not comply in any way with the requirements of these Preambles shall be rejected and shall be removed immediately from the site at the Contractor’s own expense.

No materials shall be stored or stacked on suspended floors without the Engineer’s prior approval.

  - Samples and Testing:

Every facility shall be provided to enable the Engineer to obtain samples and carry out tests on the materials and construction.  If these tests show that any of the materials or construction do not comply with the requirements of these Preambles, the Contractor will be responsible for the costs of the tests and the replacement of defective materials and/or construction.

3.9  Cement:

Cement unless otherwise specified shall be Portland Cement of a Brand approved by the Engineer and shall comply with the requirements of B.S. 12, and a manufacturer’s certificate of Test in accordance with B.S. 12 shall besupplied for each consignment delivered to the site.

Cement  may be delivered to the site either in bags or in bulk.

If delivered in bags each bag shall be properly sealed and marked with  the manufacturer’s name and shall be stored in a weatherproof shed of  adequate dimensions with a raised floor.  Each consignment shall be kept separate and marked so that it may be used in the sequence in which it is received.  Any bag found to contain cement which has set  or partly set. shall be completely discarded and not used in the works.  Bags  shall not be stacked more than 1.5m in height.

If delivered in bulk the cement shall be stored in a waterproof site  either provided by the cement supplier or by the contractor but in either case the site shall be to the approval of the Engineer.

3.10  Aggregates:

Aggregates shall conform with the requirements of B.S. 882 and the sources and types of all aggregates are to be approved in al respects by the Engineer before work commences.

-  26 –

The grading of aggregates shall be one within the limits set out in B.S. 882 and as later specified and the grading, once approved, shall be adhered to throughout the works and not varied without the approval of the Engineer.  Fine aggregate shall be clean, crushed rock  sand and coral sand, of hard quality and shall be free from lumps of stone, earth, loam, dust, salt, organic matter and any other deleterious substances.  Coral sand shall be washed in running water to the satisfaction of the Engineer.  It shall be graded within the limits of zone 1 or 2 of table 2 of B.S 882.

Coarse aggregate for concrete Grade  ‘A’, ‘B’ and ‘C’ shall be crushed blue basalt stones to the approval of the Engineer.  It shall be hard, clean and roughly  cubical in shape, non porous, free from dust, decomposed stone,  clay, earthy matter,  foreign substances or friable, thin, elongated or laminated pieces.  It shall be graded within the limits of Table 1 of B.S. 882  for its respective nominal size.  If in the opinion of the Engineer the aggregate meets with the above requirements but is dirty or adulterated in any manner it shall be screened and/or washed with clean water, if he so instructs at the Contractor’s expense.

Aggregates shall be delivered to the site in their prescribed sizes or gradings and shall be stock-piled separately on paved areas or boarded platforms in separate units to avoid intermixing, excessive segregation and contamination with other materials.  On no account shall aggregates be stock-piled on the ground.  Fine aggregates shall be allowed to drain until it has reached a uniform moisture content before it is used.

3.11  Water

The water used for mixing concrete shall be from an approved source, clean, fresh and free from harmful matter.

  - Admixtures;

No admixtures except the ones specified for waterproof  concrete shall be allowed.  The Contractor may use an approved “plasticizer” which will be added to the mixing water in the proportion recommended by the manufacturer and strictly in accordance with their written instructions, to  achieve better workability.  No additional cost will be paid for the use of the plasticiser.

CONCRETE  STRENGTHS

  - Grades of Concrete:

Grades ‘A’, ‘B’ and ‘C’ concrete shall have the following minimum strengths as given by Works Cube Test:

Grade A	Grade B	Grade C

Min. crushing) at 7 days			  21		  17		  14

strength in    ) at 28 days			  30   		   25		   20

N/mm          )

- 27-

Grade ‘D’ and ‘E’ concrete shall be of the following nominal mixes  and may be moistured either by volume or by weight.  No cube tests will be required for Grades ‘D’ and ‘E’ concrete.  These grades will be used  for un reinforced concrete, with a minimum slump of 50mm.

Grade                       D                     E

Nominal mix by		1.10		1.10 (with plums not exceeding 20% by total volume

of concrete)

Max. gauge of

coarse aggregate 		40mm*	40mm*

(* or 20mm for blinding concrete where described).

  - Maturing of Concrete Materials

Cement

The quantity of cement shall be measured by weight.  Where delivered in bags, each batch of concrete is to use one or more whole bags of cement.

Aggregate

- For Grades ‘A’, ‘B’ and ‘C’ concrete, aggregates may be measured by weight in weigh batching machine as described  hereafter.

- For Grades ‘D’ and ‘E’ concrete, aggregates shall be measured by weight or by volume.  Where measured by volume, approved gauge boxes of such a size as will give the correct proportions shall be used.

  - Weigh batching machine

Weigh batching machine shall be of an approved type and shall be properly maintained and checked for accuracy at weekly intervals.

  - Concrete Mixes ‘A’, ‘B’ and ‘C’

As specified above.

The  Contractor shall have two alternatives  to achieve the specified concrete  strengths.

  - Alternative 1  Design Mix

Contractor can use minimum amount of cement by weight per cubic metre of finished concrete as set out below,  if he provides strict with CP 110 Clause 6.5.  Requirements for design mixer.

Target mean strength.  Evidence of suitability of  proper mix proportions.

Trial mixes.

- 28 -

    - Additional Trial Mixes

The copies of this circular is available from the Engineer ‘s office  on request by the contractor.

The minimum cement content by weight shall be

Minimum cement content

per cubic metre of

finished concrete					450 kg		360 kg		250 kg

  - Alternative 2

If the contractor fails to receive the requirements of alternative 1 and/or prefers nominal volumetric mix, he shall use the following:

Mix A			Mix B			Mix C

1:13/16:2		1:1 ¾:3		1:2 ½:4

Cement				1 bag of 50 kg		1 bag of 50 kg		1 bag of 50 kg

Crushed rock sand			1 cu. ft			1¼ cu.ft		1 7//5 cu.ft

Coral sand 10mm to 5mm		½ cu. ft		7/8 cu.ft		14 cu.ft

Graded aggregates			5/8 cu.ft		7/8 cu.ft		1¼ cu. ft

20mm to 10mm

Graded aggregates			1 7/8 cu.ft		3 cu. ft			3 ¾ cu ft

Maximum water

Cement ratio				5			.56			.60

Maximum slump			50mm			50mm			50mm

Average works  strength obtained from work care  of nominal volumating mixes shall be 10% higher than the minimum concrete strengths  specified.

4.7  Ready Mix Concrete

Ready mixed concrete may be used subjects to the approval of the Engineer.

When it is used the contractor shall ensure that all the requirements of these specifications are complied with.  The Engineer may at his discretion waive temporarily the requirements of preliminary trial mixes as required  under the heading of trial mixes laid down for alternatives design mix.

- 29 -

Further to requirements the contractor shall ensure that supply and delivery of ready mixes concrete comply with the recommendations of M.S. 1926.

The  concrete shall be transported to the site in approved containers and shall be continuously agitated until it is  delivered on site.  The Contractor shall ensure that  no water is added after it is delivered.

For plant mixed concrete the contractor shall check that the delivery note for each batch shows the time when water it first added to the concrete materials, and the time interval between the delivery and the mixing of water is 20 minutes less than the final setting time of cement.

Samples of workscube shall be taken at the place where concrete is finally placed in the structural members.

4.8  Waterproof Concrete

Where “waterproof concrete” is specified,  sealocrate or other approved waterproofing  material and plasticizing agent shall be added to the mixing water in the proportion recommended by the manufacturers and strictly in accordance  their written instructions.  Waterproof concrete shall be  grade B mix and shall meet all the strength requirements  of the specified grade, except that the fine aggregate shall consist solely of rock sand.

  - Changing proportion of Aggregates

The Engineer may any time during the contract, require the  proportions of fine to coarse aggregates to be altered in order to produce a mix of greater strength or improved workability and provided that the total proportions of aggregate to cement remains unchanged, no claim for additional cost will be considered.

4.10 Testing Equipment

The Contractor shall provide the following equipment for carrying out control tests on the site:

- Straight edges 3m and 1.2m long for testing  the accuracy of the finished concrete;

- A graduated glass cylinder for use in the silt test for organic impurities in the sand;

- Slump test apparatus;

- Six inch steel cube moulds with base plates and tamping rods to B.S. 1881.

  - Work Cube Tests

Work cubes are to be made at intervals as required by the Engineer and the Contractor   shall provide a continuous record of the concrete work.  The cubes shall be made in approved 150mm moulds in strict accordance with the Code of Practice.

Six cubes shall be made on each occasion, three from different batches, of the concrete at the place where it is deposited.

- 30 -

Each cubes shall be made on each occasion, three from different batches, of the concrete at the place where it is deposited.

Each cube shall be marked with a distinguishing number (numbers to run consecutively) and the code on which it is made.  A record shall be kept on site giving the following partitioning.

- Cube No.

- Date Mode

- Location in

(d)	7-day Test

Date

Strength

(e)	28-day Test

Date

Strength

Cubes shall be forwarded by the Contractor to an approved Testing Authority, in time to be tested two at 7 days and two at 28 days.  The remaining two cubes shall be tested when necessary.

Copies of all work cube Test results shall be forwarded to the Engineer and one shall be retained on the site.

If the prescribed concrete strengths are not attained and maintained throughout the carrying out of the contract, the Contractor will be required to increase the proportion of cement and/or substitute better aggregates so as to give concrete which does comply with the requirements of the contract.  The Contractor may be required to remove and replace at his own cost any concrete which fails to attain the required strength as ascertained by Work Cube Tests.

The Contractor must allow in his rates for all expenses in connection with the preparation, conveyance to the Testing Laboratory, and testing of cubes.

CONSTRUCTION  JOINTS

  - Position of Construction Joints:

Construction joints shall be permitted only at the locations shown  on the Drawings or as instructed on the site by the Engineer.  In  general they shall be perpendicular to the lines of Principal  and shall be located  at points of minimum shear, viz vertically  at, or near, mid-spare or slabs and beams.

  - Maximum  distance between Construction Joints

Suspended slabs are generally to be east using alternative bays not exceeding 12m in length.  At least 40 hours shall elapsed between  the adjacent bays/shall be in positions to be agreed with the Engineer.

- 31 -

Beams shall be cast with the slab.  Mass concrete shall be cast in alternate bays in lengths not exceeding 7.5m and in depths not exceeding 1.5m.  Adjacent sections shall not be cast within 48 hours of each other.

Under no circumstances shall concrete be allowed to fail off but shall be deposited against stopping-boards.

  - Preparation of Construction Joints

Before placing new concrete against concrete already set, the face of the old concrete shall be thoroughly backed, roughened and cleaned, and  baitance and loose material removed therefrom.  Immediately before placing the new concrete the surface shall be  saturated with water.  A layer of mortar not less than 25mm in thickness and consisting of 1 part of cement to 1½ parts of fine aggregate shall be applied to the face of the old  concrete.  All exposed construction joints shall be treated with epory resin in accordance  with the manufacturer’s instructions.

EXPANSION/CONTRACTION  JOINT

Joints fillers and sealants shall be of an approved type unless shown on the drawings.  Reinforcement or other embedded items bonded to the concrete shall not extend continuously through any expansion/construction joint.

WATERBARS

  - Type

Waterbars shall be P.V.C waterbars of an approved type and shall be provided in the positions indicated on the drawings.

  - Joints

Joints shall be heat welded in accordance with the manufacturer’s  instructions and where the waterbar is to be fixed vertically, metal clips as manufactured by the supplier of the waterbar or of other approved design shall be provided to suspend the waterbar from the reinforcement.

  - Additional Water Bar

Where waterproof concrete is used the Contractor shall adhere strictly to the position and type of construction joints as detailed on the Drawings.  Any deviation from this procedure or the provision of additional construction joints will require the prior approval of the Engineer and any  additional waterbars which may be required will be at the Contractor’s expense.

  - Formwork to Water Bars

Formwork shall be designed with sufficient timber formers and blocking pieces to support the waterbar and to ensure that it is not displaced during concreting.  In the case of horizontal joints in vertical walling and similar members of the formwork shall be so constructed as to permit the starter or upstand of concrete surrounding  the lower  half of the waterbar to be poured in the same operation  as the slab

- 32 -

or other member from which it springs.  Formwork to walls or similar  members where a water bar is positioned at the  bags of the lift shall have sufficient  openings not less than 300mm square at approximately  225mm above the level of the waterbar to permit checking that the waterbar is correctly

positioned and not displaced during concreting.

No concreting will be permitted to portions where upstand startup from an integral part until the formwork to the starter has been fixed and approved.

8. EMBEDDED CONCRETE

All sleeves , inputs, anchors and embedded items required for  adjoining work  or for its support shall be approved by the Engineer and shall be placed prior to concreting and shall be used after an interval of time approved by the Engineer.

All contractors whose work is related to the concrete or must be supported by it shall be given ample

time and  opportunity to furnish embedded items before concrete is placed.

Expansion joint material, waterstops, and other embedded items shall be positioned accurately and rigidly.  Voids in sleeves etc. shall be  filled temporarily with readily removable material to prevent concrete entering  into them.

9. MIXING & PLACING OF CONCRETE

9.1 Concrete Mixer:

The concrete shall be mixed only in approved power driven mixers of a type and capacity suitable for the work.  Mixers shall be  of a capacity sufficient to take one whole bag of cement per batch.   Smaller size mixers  shall not be used.  The mixer shall  be equipped  with an accurate water measuring device which shall  be checked weekly for accuracy.  All materials shall be thoroughly  mixed dry before the water is added and the mixing of each batch  shall continue for a period of not less than two minutes after the water has been added and until there is a uniform distribution of the materials and the mass is uniform in colour.

The entire contents of the mixed drum shall be discharged before  recharging.  The volume of mixed materials shall not exceed the  rated capacity of the mixer.  Whenever the mixer is started,10% extra cement shall be added to the first batch and no extra payment will be made on this account.

9.2 Concrete Consistency:

As a check on concrete consistency slump tests  may be carried out and shall be in accordance with B.S 1881.  The Contractor shall provide the necessary  apparatus and allow for the costs of such tests.  The slump of the concrete made with the specified water content, using dry materials, shall be determined and the water to be added under wet conditions shall be so reduced as to give approximately the same slump.

- 33 -

9.3 Conveying of concrete:

The concrete shall be mixed as near to the place where it is required as is practicable to avoid rehandling and flowing, and only as much as be required  for a specified section of the work shall be much as is required for a specified section of the work shall be mixed at one time, such section being concerned and finished  is one operation without delay.  All concrete must be efficiently skilled and used in the works within twenty (20) minutes of mixing.  It shall be discharged from the mixer direct either into receptacles or barrows and shall be distributed by approved means which do not cause segregation or loss of ingredients or otherwise repair the quality of the concrete.  Approved mechanical means of handling will be provided they are not longer than 6m and their slope do not exceed 1 vertical to 2 horizontal is not less than 1 vertical to 3 horizontal.

9.4 Depositing of concrete

Placing of concrete in supported elements e.g slab, bed shall not be started until the concrete previously placed in top parts of columns is no longer plastic and has been in place at least for two hours.

Concrete shall be placed from a height not exceeding 1.3m directly into its permanent position and shall not be worked along the shutters to that position.  Unless otherwise approved, concrete shall be placed in a single operation to the full thickness of slabs with beams and similar members.  The  Engineer shall allow concrete to be placed for walls exceeding 150mm thickness from a height approved system of formwork is used.

In addition contractor will ensure that the concrete shall be deposited continuously such that no concrete shall  be deposited on concrete which had hardened sufficiently to cause the formation of seams or places of weakness within the section.  Placing shall be carried out at such a rate that the concrete which is being integrated with fresh concrete is still plastic.

Concrete in columns may be placed in a height of 3m with careful placing and vibration to achieve satisfactory results. Where the height of the column exceeds 3m suitable openings must be left in the shutters on that this maximum lift is not exceeded.

Concrete shall be placed continuously until completion of the part of the work between construction joints as specified hereinafter or of a part of approved extent.  At the completion of a specified or approved part a construction joint of the form and in the positions hereinafter specified shall be made.  A record of all such joints must be made by the contractor and a copy supplied to the Engineer.

9.5 Placing concrete under water

When required concrete shall be deposited under water by an approved method in such a way that the fresh concrete enters the mass of previously placed concrete from within, causing water to be displaced with minimum disturbance at the surface of the concrete.

9.6 Precautions of mixing and placing:

Any accumulation of set concrete on the reinforcement shall be removed by wire brushing  before further concrete is placed.   The contractor shall provide runways for concreting to the satisfaction of the Engineer.  Under no circumstances will the runways be allowed to rest on the reinforcement.

- 34 -

Care shall  be taken that the concrete is not disturbed or subjected to vibrations and  shocks during the setting period.

Mixing machines, platforms and barrows shall be cleaned before commencing mixing and be cleaned on every cessation of work.

Where concrete is laid on hardcore, concrete blocks or other absorbent materials, the base shall be suitably and sufficiently wetted before the concrete is deposited.

10. Compaction

Compaction:

At all times during which concrete is being placed, the contractor shall provide adequate trained and experienced labour to ensure that the concrete is compacted in the forms to the satisfaction of the Engineer.

10.1 Depth of Compaction:

Concrete shall be placed neither at a rate greater that will permit satisfactory compaction nor to a depth greater than 750m before it is  completed.

10.2 Vibration of Concrete:

During and immediately after placing, the concrete shall be thoroughly compacted by means of continuous tamping, spading, slicing  rodding, forking and vibration.  Vibration is required for all concrete of grades ‘A’, ‘B’ and ‘C’.

Care shall be taken to fill every part of the forms, to work the concrete under and ground the reinforcement without displacing it and to avoid disturbing recently placed concrete which has begun to set.

Any water accumulating on the surface of newly placed concrete shall be removed and no further concrete shall be placed thereon until such water be removed.

10.3 Internal Vibrators:

Internal vibrators shall have a frequency of not less than 7,000 cycles per minute and shall have a rotating eccentric weight of at least  2 kg.  With an eccentricity of not more than 12mm.  Such vibrators shall  visibly affect the concrete within a radius of 22mm from the vibrator.

Vibrators shall not be used to move concrete from place to place in the formwork.

At least one internal vibrator shall be operated for every two cubic metres of concrete placed per hour and at least the spare vibrator shall be maintained on site in case of break-down during concreting  operations.

- 35 -

10.4 External Vibrators

External formwork vibrators shall be of the high frequency less amplitude type applied with the principal direction of vibration in the horizontal plane.  They shall be attached directly in the forms at not more than 1.2m centers.

In addition to internal and external vibration the upper surface of suspended floor slabs shall be levelled with a tamping vibrating speed prior to finishing.  Vibrating elements shall be of the low frequency high amplitude type operation at speed of not less than 3,000 r.p.m.

11.Curing and Protection

11.1 Periods and means of curing and protection:

Care must be taken that no concrete is allowed to become prematurely dry and the fresh concrete must be carefully protected within two hours of placing from rain, sun and wind by means of massive sacking, polythone sheeting, or other approved means.  The protective layer  and the concrete itself must be kept continuously wet for at least  seven days after the concrete has been placed.  The Contractor must allow for the complete covering of all fresh concrete for a period of 7 days.  Heasian or polythene sheeting shall be in the maximum widths obtainable and shall be secured against wind.  The Contractor will not  be permitted to use old  cement bags, hessian or other material in small piece.

11.2 Protection of foundation concrete

Concrete in foundations and other underground work shall be protected from admixture with falling earth curing and after placing.

11.3 Executive loads before curing

Traffic or loading shall not be allowed on the concrete except with the written permission of the engineer.

12. Faulty Concrete

Any concrete which fails to comply with these preambles or which shows signs of setting  before it is placed shall be taken out and removed from the site.  Where concrete is found to be defective after it was set, the concrete shall be out and replaced in accordance with the Engineer’s instructions.  On no account shall any faulty,  honeycombed, or otherwise defective concrete be repaired or matched until the Engineer has made an inspection and issued instructions  for the repair.  The whole of the cost whatsoever, which may be occasioned by the need to remove faulty concrete shall be borne by the contractor.

13. Reinforcements

13.1 Type of Reinforcement:

The steel reinforcement shall comply with the latest requirement of the following British Standards:

Round mild, medium tonsile and to B.S 765 (Imperial units) high tonsile and steel bars.

- 36 -

Hot rolled bars for the reinforcement 				to B.S 1449 (metric units)

of concrete

Cold twisted steel bars					to B.S 1144 (imported units)

Cold worked steel for the reinforcement			to B.S 4461 (metric units)

of concrete

Fabric reinforcement						to B.S 1221

It shall be in Imperial or Metric sizes as detailed on the drawings.

13.2 Testing of Reinforcement

If required by the Engineer the contractor shall submit a test certificate of the rollings, and/or shall arrange for testing by MOW or other approved authority.  Reinforcement shall be free from loose mill scale or rust, grease, paint or other substance likely to reduce the bond between the steel and  concrete.

13.3 Fabric Reinforcement

It shall be of size and/or weight specified and shall be tied with other reinforcements with minimum 225mm laps, using no. 19 S.W.C annealed binding wire.

13.4 Fixing and Reinforcement:

Reinforcement shall be accurately  bent to the shapes and dimensions shown on the Drawings and/or schedule and in accordance with B.S. 1478.  Reinforcement must be cut and bent  sold and no welded joints will be permitted unless so detailed.  Reinforcement shall be accurately placed  in position as shown on the drawings and shall be secured against displacement by using No. 18 S.W.C annealed binding wire or  suitable clips at inter-sections and laps, and shall be supported by concrete or metal supports, steel chairs, spacers or metal hangers to ensure the correct position and cover before concreting and shall be kept in the same position during concreting.  However such supports, chairs etc.  shall have minimum 12mm cover made of concrete blocks where  the concrete surface is exposed to weather and/or without finishes.

No laps shall be permitted except the  acres shown on the drawings without the prior approval of the engineer.

13.5 Spacing Blocks:

Spacing blocks of approved size and shape made of concrete similar to that used in the surrounding construction and fixed to the reinforcement or formwork by No. 18 S.W.C wires set into the spacer blocks or other  approved means shall be provided where necessary to ensure that the requisite cover is obtained.  The contractor is to include for providing sufficient such spacer blocks in his prices for steel reinforcement when such supplier has been nominated.

- 37 -

Where composite blocks or minor forms from construction are just spare block are to be provided.  These will generally  consist of concrete blocks as described above made to fit the width of the rib less 3 mm of reinforcement bars used  per on the top surface with wire ties at each

13.6 Concrete cover to reinforcement:

Unless otherwise instructed the concrete cover to rod reinforcement over  main bars in any face shall be:

Foundations against each face					3     (75mm)

Foundations against blinding						2     (50mm)

Columns								1½   (38mm)

Beams									1      (25mm)

Slabs									½      (13mm)

13.7 Positions and correctness of reinforcement:

No concreting shall be commenced until the engineer has inspected the reinforcement in position and until he has approved the same.  The contractor shall give two celar days notice of his intention to concrete.

Irrespective of whether any inspection and/or approval of the fixing of the reinforcement has been carried out as above, it shall be the contractor’s sole responsibility to ensure that the reinforcement complies with the details on the drawings or schedule and is fixed exactly in the positions shown therein and in the positions to give the prescribed cover.

The contractor will be held entirely responsible for any failing or defect in any portion of the reinforced concrete structure and including any consequent   claims, third party claims, etc, where it is shown that the reinforcement has been incorrectly positioned or is incorrect in size or quantity with respect to the detailed Drawings or schedules.  Unless permitted by the Engineer, reinforcement shall not  be after being embedded in hardened concrete.

13.8 Protection of exposed reinforcement

Where reinforcement projects frame concrete setting of the structure and this reinforcement is executed  to remain exposed to more than a month it is to be with  a cement  to prevent rust staining on the finished concrete.  This is to be brushed off the reinforcement prior to the continuation to converting.

The Contractor shall be responsible for the co-ordination with the Electrical and other sub-contractors for incorporating electrical conduit,  pipes, fixing locks, chases, holes and the like in concrete members as required and must ensure that adequate notice is given to sub-contractors informing them when concrete members incorporating the above are to be poured.  The contractor shall submit full details including position of these items to the Engineer for approval before the work is put in hand.  All fixing blocks, chases, holes, etc, to be left in the concrete shall be accurately set out and cast with the concrete.

- 38 -

15. Position of  electrical conduit

Unless otherwise instructed by the Engineer an electrical conduit to be positioned within the reinforced concrete shall be fixed inside the steel cages of beams and columns and between the top and bottom steel layers in slabs and similar members.  No conduits are to be placed into concrete members having a  dimension less than 100mm.

The proposed position of all electrical conduits 25mm and over in diameter which are to be enclosed in the concrete shall be shown accurately on a plan to be submitted to the Engineer, whose approval shall be obtained before any such conduit is placed.

16. Formwork

16.1 Materials and Design

Formwork shall be constructed of timber or steel or precast concrete or other approved material with sufficient strength to withstand pressure resulting from placing and vibration of the concrete and with  rigidity to achieve the specified tolerances.

The design and Engineering of the formwork as well as its construction shall be the  responsibility of the contractor.  The Formwork shall be designed for the loads,  laterial pressure, pressure  due to cyclonic winds and  other loads likely to be encountered on site.

Shops drawings for formwork including the location and reshoring shall be submitted for approval by the Engineer before erection.

16.2 Construction

All formwork shall have joints close enough to prevent leakage of liquid from the concrete and formwork  shall be jacked or dedged and clamped or bolted to permit adjustments before concreting and to permit easing and removal of formwork without jarring the concrete.  Formwork shall be securely braced and strutted against lateral deflections and vertical movements.   Where formwork is supported on previously constructed portions of the reinforced concrete structural frame, the Contractor shall by consultation with the Engineer ensure that the supporting concrete structure is capable of carrying  the load and/or is sufficiently propped from lower floors or portions of the frame to permit the load to be temporarily  carried during construction.

Formwork shall be cambered to compensate for anticipated deflections prior to hardening of the concrete.

16.3 Preparation for Concreting

The Contractor’s attention is drawn to the various surfaces textures and applied finishes required and the faces of the formwork next to the  concrete must be of such material and construction and be sufficiently true to provide a concrete surface which will in each particular case permit the specified surface treatment or applied finish.

- 39 -

At construction points contact surface of the form squeating for flush surfaces shall overlap 300mm and shall hold right against the hardened concrete to prevent effects or loss of mortar.

Methods of fixing and positioning of the formwork which results in holes through the concrete and/or left in metal ties or similar in the concrete shall require Engineer’s approval.

All surfaces which will be in contact with concrete shall be piled or greased to prevent adhesion of mortar.  Oil or grease shall be of a non-staining mineral type applied as a thin film before the reinforcement is placed.  Surplus moisture shall be removed from the forms prior to placing of the concrete.

Temporary openings shall be provided at the base of columns, wall and seam forms and at any other points where necessary to facilitate cleaning, and inspection immediately before the pouring of concrete.  Before the concrete is placed the shuttering shall be trued-up, and the interior of the form shall be completely cleared of all extraneous materials including accumulated water.

The reinforcement shall then be inspected for accuracy of fixing, immediately before placing the concrete the formwork shall be well wetted and inspection openings shall be closed.

16.4 Defective Formwork:

Defective formwork shall be removed or strengthened and improved by the contractor according to the instructions by the Engineer.

16.5 Formwork to Construction Joints etc.

Formwork forming the construction joints and expansion joint shall be rigid, tight to avoid loss of mortar and true in square.

Formwork shall be inspected and passed by the Engineer before placing reinforcement and concreting.

16.6 Stripping Formwork:

Formwork shall be removed without undue vibration or shock and without damage to the concrete.  No formwork shall be removed without the prior consent of the Engineer and the minimum periods that shall elapse between the placing of the concrete and the striking of the formwork will be as follows:

Beam side  walls and columns (unloaded)						2 days

Slab soffits (with props designed to left under)					7 days

Beam soffits (with props designed to left under)					10 days

Subject to work cubes achieving the specified strengths and the loads due to construction on them being lighter than the designed loads.  The props can be removed for:

Slab  ……..	………	………..	10 days

Beams		………	………..	21 days

- 40 –

If the Contractor wishes to take advantage of the shorter stripping times as permitted above for beam and slab soffits when propos are left in place, he must so design his formwork that sufficient props as agreed with the Engineer can remain in their original position without being moved in any way until expiry of the minimum time for removal of props.  Stripping and re-propping will not be permitted.

Contractor shall be responsible for consequent damage arising from early stripping of form work.

16.7 Making  good:

After removal of formwork all projections,  etc, on the concrete surface  shall be chipped off, and made good to the requirements of the Engineer.  Any voids or honeycombing shall be treated as described in “faulty concrete”.

16.8 Fair-face etc.

Where fair-face is specified the contractor shall make a sample of area formed by sides not less than 1.2m for approval by the Engineer and the Architect.  Same will apply to Board Marked.  Tamped and   finishes.

16.9 Related Uniformed Surfaces

Top of walls or buttresses, horizontal offsets and similar unformed surfaces occurring immediately adjacent to formed surfaced shall be struck smooth after the concrete is placed and shall be floated to a texture  reasonably insistent with that of the formed surfaces.

17. PRECAST CONCRETE

17.1 General Requirements

Unless otherwise approved by the Engineer, all precast concrete construction shall be carried out on the site and shall conform to requirements given elsewhere in these preambles.

The maximum size of coarse aggregate in precast concrete shall not exceed 20mm except for thickness less than 75mm where it shall not exceed 12mm.

The compacting of precast concrete shall conform with requirements given elsewhere in these preambles except for thin slabs where use of immersion type vibration is not practicable.  The concrete in those slabs may be consolidated on a vibrating table or by any other methods approved by the Engineer.

17.2 Steam Curing

Steam curing of precast concrete will be permitted.  The procedure for steam curing shall be subject to the approval of the Engineer.

The precast work shall be made under cover and shall remain under the same cover and shall remain under the same for seven days.  During this period and for a further seven days the concrete shall be shielded by sacking or other approved material kept constantly wet.  It shall then be stacked in the

- 41 -

open for at least a further seven days to season before being set in position.  Where steam curing is used these times may be  reduced subject to the approval of the Engineer.

17.3 Method of Handling:

Precast concrete units shall be constructed in individual forms.  The method of handling the precast concrete units after casting, during curing and during transport and erection shall be subject to the approval of the Engineer, providing that such approval shall not relieve the Contractor of responsibility for damage to precast concrete units resulting from careless handling.

17.4 Repairs:

Repair of damage to the precast concrete units, except for minor abrasions of the edges which will not impair the installation and/or appearance of the units will not be permitted and the damaged units shall be replaced by the Contractor at his own expense.

17.5 Moulds

Except where precast work is described as “fair-face” the moulds are to be made of metal or are to have metal or plywood linings or are to be other approved moulds which will produce a smooth dense fair face to the finished concrete suitable to receive a painted finish direct  and free from all shutted marks, holes, pittances, etc.  In his prices for such precast work the Contractor shall include for all rubbing down to produce the finish required to the satisfaction and approval of the Engineer and the Architect.

Where precast work is to have an exposed aggregate as finish the moulds shall be constructed to the requirements given for moulds for “fair face” work.  The method of achieving the exposed aggregate finish shall be the aggregate transfer or other approved methods.  A sample showing the required finish and shape shall be approved by the Architect/Engineer.

The precast units shall be installed to the lines, grades and dimensions shown on the Drawings or as directed by the Engineer.

18. COMPOSITE FLOOR SLABS

18.1 Size, type and concrete mix for floor block:

Concrete hollow blocks for use in the composite floor slabs are to be size and shape as shown on the Drawings with 25mm wall thickness and are to be of adequate strength to support the concrete during placing and consolidation by vibration.  Blocks are to be manufactured in accordance with the procedure specified in B.S 2028 and to be of a mix not weaker than 1:10 cement: combined aggregates using maximum 10mm size aggregate.  No coral sand shall be used in making of concrete blocks.

Concrete blocks are to be cured for at least 28 days before use of the site.  During the first seven days of curing, blocks are to be kept permanently damp and protected from exposure to sun and wind.

Concrete blocks are to be well wetted before the pouring of concrete.

- 42 –

18.2 Composite Floor Construction

The hollow block floor construction is generally to be as shown on the Engineer’s Drawings.

Care shall be taken in placing blocks to ensure that they are set out in accordance with the details shown on the Drawings and that they run truly in line without encroaching on the width of the in-situ ribs.

The open ends of hollow blocks adjacent to the concrete to be placed in-situ are to be plugged or stopped previously with mortar or concrete to prevent the concrete from flowing into the void and the contractor is to include for this in his prices.

The Contractor should note that slip tiles are not to be used to the soffit of ribs and he is to take this into consideration in pricing the items of formwork to the soffit of hollow block floor construction.

Before concreting is carried out the blocks are to be thoroughly wetted.

Care should be taken during concreting that the width of ribs between the rows of blocks and of the solid in-situ concrete shown on the Drawings adjacent to supporting beams is not encroached upon by the blocks.  It is essential that the concrete topping be poured at the same time as the ribs between hollow blocks.

18.3 Fixing of rib reinforcement

Reinforcement shall be positioned accurately with required cover in accordance with the Drawings and using the particular spacing blocks with wire ties as previously described.  Spacer blocks shall be provided in ribs at not more than 1.2m centres.  Care must be taken during concreting that the reinforcement is not displaced.

Where holes for services, etc. occur, the necessary holes or pockets shall be accommodated by the replacing of a hollow block by in-situ concrete or the widening of a rib all in accordance with the Engineer’s instructions.   Prices for holes, etc. through hollow block construction are to include the re-arrangement or substitution of the hollow block with solid concrete in addition to the actual formation of the hole.

19. NOTES CONCERNING MEASUREMENT AND PRICING

The Contractor must allow for all costs incurred during the progress of the Contract for complying with the provisions concerning the preparation and use graded mixes.

Prices for concrete shall include for mixing and depositing as described or indicated and for hoisting and depositing at the various levels required throughout the building, and shall also include for forming or hacking a satisfactory key for all faces receiving asphalt and plaster work.  Prices for slabs shall also include for levelling off the surface as described under “compaction”, and all temporary formwork to form construction joints at bay edges.

Prices for reinforced concrete shall, in addition, include for filling into, between or on formwork and thoroughly compacting between and around rods or fabric reinforcement and for forming all additional

- 43 –

construction joints between  varying mixes.  Where described as vibrated, prices must include for fully vibrating as described.

Formwork (use and waste only is measured net to the actual surface of the concrete to be supported and the prices for formwork shall include for extra material at joints, extra labour  and waste for narrow widths, small quantities, overlaps, passings at angles, straight cutting and waste,  splayed edges, notchings, etc and for fixing at the various levels  including  battons, struts and supports and for bolting, jacking, wedging, easing  striking and removal.  Prices for linear items such as boxings shall include for angles and ends.  Strutting has been measured at varying levels to slab soffits only and prices  for other items must include for strutting at any level.

Prices for steel rod reinforcement shall include for cutting to lengths and all labour in bending and cranking, forming hooked ends, handling, hoisting and fixing in position and for providing all necessary tying wire and supports.  Prices for fabric reinforcement shall include for all straight cutting and waste, handling, hoisting and fixing in position, providing all necessary tying wire, and supports and all extra material in laps.

- 44 –

INDEX

1.   GENERAL

1.1   Scope

1.2   Definitions

1.3   Responsibility

2.   EXCAVATION

  - Inspection in-site

  - Dealing with water

  - Excavation Dimensions

  - Rock

  - Blasting

  - Bottoms for excavations to receive foundations

  - Hardcore filling

  - Materials found in excavations

3.   CONCRETE WORK

  - Architect/Engineer

  - Code of Practice

  - Supervision

  - Contractor’s Plant, Equipment and Construction Procedures

  - Level and Foundations

  - Tolerances

  - Materials Generally

  - Samples and Testing

  - Cement

  - Aggregates

  - Water

  - Admixtures

4.   CONCRETE STRENGTHS

4.1		Grades of concrete

4.2		Measuring of concrete materials

4.3		Weigh batching machine

4.4		Concrete mixes A,B and C

4.5		Alternative 1: Design mix

4.6 	Alernative 2: Volume mix

4.7		Ready Mix Concrete

4.8		Waterproof Concrete

4.9		Changing Proportions to Aggregates

4.10	Testing Equipment

4.11	Work Cube Tests

- 45 –

5. CONSTRUCTION JOINTS

  - Position of construction joints

  - Maximum distance between construction joints

  - Preparation of construction joints

6.      EXPANSION AND CONTRACTION JOINTS

7.      WATERBARS

  - Type

7.2    Joints

7.3 	Additional waterbars

7.4 	Formwork waterbars

8.     EMBEDDED CONCRETE

9.    MIXING AND PLACING OF CONCRETE

  - Concrete mixer

  - Concrete consistency

  - Conveying of concrete

  - Depositing of concrete

  - Placing of concrete under water

  - Precautions for mixing, conveying and depositing concrete

10.    COMPACTION OF CONCRETE

  - Depth of compaction

  - Vibration of concrete

  - Internal vibrators

  - External vibrators

11.    CURING AND PROTECTION

  - Periods and means of curing and protection

  - Protection of foundation concrete

  - Excessive loads before curing

12.    FAULTY CONCRETE

13.     REINFORCEMENT

  - Types of Reinforcement

  - Testing of Reinforcement

  - Fabric Reinforcement

  - Fixing of Rod Reinforcement

  - Spacing Blocks

- 46 –

  - Concrete cover to Reinforcement

  - Position and correctness of Reinforcement

  - Protection of exposed Reinforcement

14.     CHASES HOLES ETC. IN CONCRETE

15.     POSITION OF ELECTRICAL CONDUITS IN CONCRETE

16.     FORMWORK

  - Materials and Design

  - Construction

  - Preparation for Concreting

  - Defective Formwork

  - Formwork to construction joints etc.

  - Stripping of formwork

  - Making good

  - Fairface etc.

16.9	Related unformed surfaces

17.     PRECAST CONCRETE WORK

  - General Requirements

  - Steam Curing

17.3	Method of Handling

  - Repairs

  - Moulds

18.     COMPOSITE FLOOR SLABS

  - Size, Type and concrete mix for floor blocks

  - Composite floor construction

  - Fixing of rib reinforcement

19.     NOTES CONCERNING MEASUREMENT AND PRICING CONCRETE WORK

In lump sum contracts, delete “Bill of Quantities” and replace with “Activity Schedule.”

The sum of the two coefficients Ac and Bc should be 1 (one) in the formula for each currency.  Normally, both coefficients shall be the same in the formulae for all currencies, since coefficient A, for the nonadjustable portion of the payments, is a very approximate figure (usually 0.15) to take account of fixed cost elements or other nonadjustable components.  The sum of the adjustments for each currency are added to the Contract Price. [To be transferred to the User Guide]