## Summary Bill No. 2
Item | Description | Total (MUR)
A | Total carried from Bill No. 2 - Photovoltaic (PV) System - DBM Triolet:
| Item no 1 - Generals | 0
| Item no 2 - Photovoltaic (PV) System | 0
| Item no 3 - Remote monitoring | 0
| Item no 4 - Earthing and Equipotential Bonding | 0
| Item no 5 - Miscellaneous | 0
B | Engineer's Contingency: Sum for contingencies to be expended or deducted in whole or in part at the discretion of the Engineer/Project Manager | 600000
TOTAL CARRIED FORWARD TO MAIN SUMMARY

## Bill No. 2
Item | Description | Unit | Qty | Rate Supply (MUR) | Rate Install (MUR) | Total (MUR)
1 | Generals
Preamble
This section describes the requirement for rooftop-mounted photovoltaic (PV) system for DBM buildings at Triolet.
The Bidder is required to undertake a survey of the DBM buildings at Triolet prior to submission of bid document and is required to submit report highlighting any discrepancy and new works, clash with existing/new services/structures and status/suitability of rooftops for successful installation of the PV farm.
1.1 | Allow for planning , coordination and marking on-site with the Civil/Builder Contractor for all builders works (including but not limited to chasing, coring, access traps, making good, trenches) required to be carried out for the PV system installation. | Lot | 1 |  |  | 0
1.2 | Allow for 'Danger Electricity' warning signs, Health and Safety procedures sign, Emergency procedures sign, isolation and earthing procedures, First Aid signs in all plantrooms and associated electrical switchboards. | Lot | 1 |  |  | 0
| Carried to Summary |  |  |  |  | 0
2 | Photovoltaic (PV) System
2.1 | Supply, Install, Test and Commission a PV system as described in Specifications and Drawings. The PV system shall consist of:
2.1.1 | Rooftop-mounted PV modules as per technical specifications. - Bidder to confirm module type and peak power (Wp). The total solar PV array capacity should not be less than the designed capacity (kWp). | Lot | 1 |  |  | 0
2.1.2 | Three phase DC/AC Inverters c/w surge arresters for AC and DC (to be waterproof if mounted externally). | Lot | 1 |  |  | 0
2.1.3 | Support structure for the modules | Lot | 1 |  |  | 0
2.1.4 | Support structure of inverters, enclosures and distribution boards including shades | Lot | 1 |  |  | 0
2.1.5 | Solar DC cables to connect PV modules and to the inverters for a complete operational circuit c/w conduits, clamps and low-impedance, proprietary cable terminations and joints for all cable connections to minimise losses. | Lot | 1 |  |  | 0
2.1.7 | Supply and install cable tray/ladder/racks as appropriate to withstand the UDL of cables, made of hot dipped galvanised steel, straight or curved, jointed by rustproof bolts and bonding jumper, c/w fittings, accessories, supports manufactured by 2.5 mm the hot dipped galvanised U channels similar to Unistrut (Cabstrut), installed to any background for main cabling all as specified and detailed. Cover, where required shall be of hot dipped galvanised manufacture of minium thickness 1.5mm. | Lot | 1 |  |  | 0
2.1.8 | Supply and Install PVC sleeves/conduits as required on the roof. Contractor to ensure sleeves are UV protected and are resistant to outdoor enviroment conditions. | Lot | 1 |  |  | 0
2.1.9 | Allow for all necessary accessories and fittings to allow safe operation, maintenance and servicing of the system on the roof (work at height), including thermometers, hooks, anchor points, pulleys, and the like. | Lot | 1 |  |  | 0
2.1.10 | Any other item that may be required for a fully functional system to meet the Client's requirement (breakdown to be provided). | Lot | 1 |  |  | 0
2.1.11 | Supply and install cat/ship ladders for roof access | Lot | 1 |  |  | 0
| Carried to Summary |  |  |  |  | 0
3 | Remote monitoring
DBM Energy Ltd shall have a remote contol command center for monitoring of the PV System at each DBM site.
3.1 | Contractor to allow for integration of proposed PV system monitoring software to DBM's remote monitoring platform. | Lot | 1 |  |  | 0
3.2 | Allow for connection to DBM Triolet Local Area Network (LAN). Communication protocol to be IP based. | Lot | 1 |  |  | 0
3.3 | Supply and Install IP gateways for connection to DBM Triolet Local Area Network (LAN). | Lot | 1 |  |  | 0
3.4 | Supply and Install enclosures as per technical specifications for IP gateways. | Lot | 1 |  |  | 0
3.5 | All the required control cables required for a functional system and for remote monitoring. | Lot | 1 |  |  | 0
3.6 | Any other item that may be required for a fully functional system to meet the Client's requirement. | Lot | 1 |  |  | 0
| Carried to Summary |  |  |  |  | 0
4 | Earthing and Bonding
Supply and install the following as per drawings and specifications.
4.1 | Supply and install earthing system for the PV system which shall include copper rods, matts, tapes, cables etc. as appropriate, inspection pits c/w integral earth bars, earth bars with disconnecting link, ground enhancing materials to achieve an earth resistance of <5ohms. | Lot | 1 |  |  | 0
4.2 | Allow for bonding of all exposed and extraneous metal parts to the main eathing system. | Lot | 1 |  |  | 0
| Carried to Summary |  |  |  |  | 0
5 | Miscellaneous
5.1 | Testing and commissioning the whole of the foregoing installation in accordance with the specifications and relevant BS. | Lot | 1 |  |  | 0
5.2 | Allow for training of Operator's personnel in Operation and Troubleshooting of the complete installation as per tender specifications | Lot | 1 |  |  | 0
5.3 | Contractor to provide O&M manual with all information as specified in 3 Hard-copies and 3 soft copies on digital media. | Lot | 1 |  |  | 0
5.4 | Contractor to allow for submission of shop, construction and as-made drawings in printed copy and soft CAD and PDF copy. | Lot | 1 |  |  | 0
| Carried to Summary |  |  |  |  | 0