##### TAMIL NADU WATER SUPPLY AND DRAINAGE  BOARD

TECHNICAL SPECIFICATIONS

Name of Work:  Package-2 (Zone-VII) - Providing UGSS to Added Areas namely Kavundampalayam and Thudiyalur Area Wards 1(pt), 2 to 9 (Zone VII) of Coimbatore Corporation in Coimbatore District for implementation of Collection System. Pumping Main, Pumping Station, Lift Stations, Machine-holes, Ventilating Shafts, Pumpsets, House Service Connections, Road Restoration (Period of Completion- 36 months, Trial Run and commissioning - 6 months and Paid maintenance for 5 years).

Technical Specifications

# Index

| Sl. No. | # Description | Page No. |
| --- | --- | --- |
| I | SCOPE OF WORK | 3 |
| II | GENERAL SPECIFICATIONS | 4-11 |
| III | CIVIL WORKS | 12-16 |
| IV | SPECIAL SPECIFICATION FOR SEWERAGE WORKS | 17-26 |
| V | PIPE LAYING WORKS | 27-37 |
| VI | LIQUID RETAINING STRUCTURES | 38 |
| VII | TESTING, ERECTION, TRIAL RUN, COMMISSIONING AND ACCEPTANCE | 39-43 |
| VIII | ELECTRICAL WORKS AND PUMPING MACHINERY | 44-54 |
| IX | PUMP SETS AND ACCESSORIES | 55-59 |
| X | OPERATION AND MAINTENANCE PERIOD | 60-72 |
| XI | REFERENCE TO SPECIFICATION / CODE OF PRACTICE | 72-75 |
| XII | ENVIRONMENTAL MANAGEMENT PLAN FOR UGSS PROJECTS | 76-80 |
| XIII | RESETTLEMENT PLAN | 81 |
| XIV | MATERIAL TESTING SAMPLING PROCEDURE | 82-90 |

I. SCOPE OF WORK

1.0 Introduction :

Coimbatore Corporation in Coimbatore District of Tamilnadu has at a latitude of 100 58’00” North and Longitude of 760 58’00” East.  It is headquarter of Coimbatore District which is situated at 495 Km from Chennai and surrounded with The Nilgiris District in the North, Kerala State in the West, Thiruppur and Erode Districts in the East and Dindigul District in South. Kavundampalayam &Thudiyalur Town areas are part of Coimbatore Corporotion with STP works and Wards 1(part), 2 to 9 and 43(part)-ZONE VII wards respectively and located at about 6 Km from Coimbatore City.  An underground sewerage scheme has been formulated for these areas and for the collection system and sewage treatment Plant,. The underground sewerage scheme is designed for a pro-rata sewage contribution of 115 lpcd. The street sewers, pumping mains and preliminary treatment units have been designed for the contributory sewage flow expected during ultimate stage.. for intermediate stage. Design of the sewage collection system has been performed to the extent possible, by gravity assistance. The sewage collection system is designed based on contributing population and proportionate sewage generated in the branch lines. Sewage collected in the lift/pumping stations will be conveyed to the treatment plant for treatment and final disposal.

.1.Collection System :

- Supply, laying and jointing of DWC pipes of 150mm to 300 mm dia, CI Pipes of size 200mm dia to 700 mm dia and including earth work excavation & refilling and restoring the road surface.

- Construction of appurtenances like machine-holes and drop machine-holes

Confirmatory survey for all zones should be done by the Contractor before proceed the execution work.

2. Pumps , Pumping Station & Pumping Main:

- It is proposed to provide Pumping station with pump sets,Pumping mains and allied works .

- Providing 1 DWF pumpsets

- The pumpsets of Non clog submersible type for pumping combined quantity of sewerage.

- Providing  Diesel Generator set in  pumping station .

- Construction of screen well, grit chamber and suction well.

- Pump rooms

- Compound wall.

3. Miscellaneous:

The bidder shall submit two copies with one set of originals of completion plans & LS plans as executed with all the details for all items of work including sewage system, pumps, pumping main & pumping station.  The bidder shall also submit all the above in a compact disc  format (in AutoCAD –R12/14) in a suitable readable scale as approved by the Engineer.

The bidder shall also submit two copies (as per the contract data) operation & maintenance manual for all Electro –Mechnical items involved in the main pumping station for proper maintenance of the system in future

GENERAL SPECIFICATIONS

INTERPRETATION :

In this contract the following works shall be understood as having the meaning hearein assigned to them.

a)	“The Board” means the Tamilnadu Water Supply and Drainage Board, a statutory body constituted under Tamilnadu Water Supply    and Drainage Board Act 1971 having its office at No.31, Kamarajar Salai, Chepauk, Chennai-600 005  and any officer duly authorised by this Board to act on its behalf.

- “Contractor” means the person or persons or firm or company contracting for the work specified, including his or their executors or administrators or legal representatives or successor.

- “Engineer” means Chief Engineer or his representatives or any other Engineer appointed from time to time by    the Board to act as such in connectionl with these works.  Whenever any  work is specified to be done or materials supplied to the satisfaction of the Engineer, it shall be taken as including his properly authorised assistance and duly  authorised representatives.

- “Works” means works to be constructed, completed and maintained  in accordance with contract.

- TNBP – Tamilnadu Building Practice

- IS – Indian Standard

- ISS – Indian Standard Specification

- BIS – Bureau of Indian Standards

- SS – Standard Specifications of Tamil Nadu Building Practice Specifications.

II GENERAL SPECIFICATION FOR MATERIALS

All materials required for the works shall be procured and supplied by the contractor himself. The materials shall be of good quality and conforming to relevant BIS. The materials which are classified for ISI marking should be supplied with ISI marking only.

1.	Cement and Reinforcement :

1.1	The entire quantity of cement and steel required for the work will be procured by the contractor . The contractor is responsible for all transport and storage of the materials and shall bear all related cost. The Employer shall be entitled at any  reasonable time to examine the cement and steel supplied by the contractor.

1.2	 The cement procured by the contractor shall comply with the requirements of  IS 269/ 1976  with the latest revision thereof for ordinary portland cement and IS 8112/ 1989 with the latest revision thereof for 43 grade ordinary portland cement and IS 12330/ 1988 with the latest revision thereof for Sulphate resisting Portland cement. It shall be of the best normal setting quality unless specially rapid hardening or quick setting quality if expressly instructed by the Engineer to be supplied. Each bag shall bear ISI Certification mark and as per specification no. 10 of TNBP volume I.

1.2.1	The cement procured by the contractor shall comply with the requirements of  IS 12269/ 1987  with a designed strength for 28 days being a minimum of 53 MPa or 530 kg/sqcm. 53 Grade OPC provides high strength and durability to structures because of its optimum particle size distribution and superior crystallized structure.

1.2.2	The cement procured by the contractor shall comply with the requirements of  IS 12330/ 1988. It is a type of Portland cement in which the amount of tricalcium aluminate (C3A) is restricted to lower than 5% and (2C3A+C4AF) lower than 25% which reduces the formation of sulphate salts.The reduction of sulphate salt lowers the possibility of sulphate attack on the concrete.

1.3	All cement shall be procured in bags and shall be stored in a dry place for which the contractor shall be responsible.  Consignment of bagged cement shall be properly stacked in a manner which will permit easy access for inspection and definite identification. Cement shall be used in approximately in  the chronological order in which it is received, but cement that has been stored for a period longer than 4 months from the date of initial sampling shall not be used  unless it has been retested at the expenses of the contractor and passed by the Engineer  as good quality on the retest. Cement aged more than 180 days from the date of initial sampling shall be rejected.

1.4	Cement which has become caked or perished shall on no account be used on the works and shall be rejected.  Although the Engineer may have passed any consignment, he shall however have the power at the subsequent time to reject such consignment if he finds that any deterioration in the quality thereon has taken place.

1.5	The steel bars  shall comply with the requirements set forth  in the IS 13620-1993  with the latest revision thereof and the test as described for ultimate  tensile strength, bond test and elongation tests. The steel bars should be only Fusion bonded Epoxy coated  as per IS specification. It is mandatory to use Fusion bonded Epoxy coated  steel reinforcing bars  for all  structures.

All reinforcing steel shall be clean and free from oil, grease, loose scales or rust or other coatings of any character which would reduce or destroy the bend. Each bundle containing the bars shall  bear the ISI Certification mark.

1.6	All the samples of construction materials should be Tested in the Meterial Testing Laboratories located  with in the region  ( Coimbatore) to ensure the quality of the material. If the sample  could not be tested in the Coimbatore Laboratory due to some  unavoidable  reasons, the sample may be Tested in any one of the other 3  Materials  Testing  Laboratories located at  Madurai, Trichy and  Tindivanam. Two samples should be  taken by the Engineer  in the presence of the contractor or his authorised representatives or  the technical personnel employed by the Contractor as in the agreement.  The contractor shall without extra cost provide samples and cooperate in the testing of the cement/steel.  One sample shall be got tested and the other sample shall be retained by making clear identification in the sample by the Engineer  so as to identify at a later date.  The cost of such test shall be borne by the contractor.

1.7	A record of the quantity of cement/ steel  procured with the name of dealer, bill number and date shall be maintained by the contractor. This should be produced for examination by the Engineer at any time. The age of the cement shall be reckoned from the date of  manufacture and it shall be verified by the Engineer.

1.8	The rejected  consignment of cement and steel should be removed from the site within two days.

Bricks:

a. 	Manufacture :

Common burnt clay building bricks shall conform to the requirements of IS 1077 and shall be of quality not less than  class 50 with moisture absorption rate not exceeding 15% as defined in IS : 1077.  The bricks shall be chamber burnt and shall not be damaged in any manner and sizes shall conform to the works sizes specified with tolerances as given in 6.2 of IS:1077.

b.  	Samples :

The Contractor shall deliver samples of each type of brick to the Engineer, and no orders shall be placed without the written approval of the Engineer.  All the bricks used in the works shall be of the same standard as the approved samples.  The samples shall be preserved on site, and subsequent deliveries shall be checked for uniformity of shape, colour and texture against the samples.  If in the opinion of the Engineer any deliveries vary from the standard of the samples, such  bricks shall be rejected and removed from the site.

c.  	Uniformity :

The  bricks selected for exposed pointed brickwork walls shall be of uniform colour, deep cherry red or copper colour and uniform texture.  Only such bricks as are permitted by the Engineer shall be used.

d.  	Testing :

Samples of the bricks shall be tested in accordance with IS : 3495 by the Contractor for compliance with the aforesaid, before any order is placed, and soon after receipt of a consignment.  Tests shall be carried out as and when required by the Engineer on samples selected by the Engineer’s representative.

e.  	Laying :

Brickwork shall be uniformly bedded, bricks being laid upwards.  Each brick shall be floated and rubbed in upon such sufficient quantity of mortar that the mortar is squeezed up into the joints, but if such joints are not filled with mortar by this process they shall be flushed up with the mortar from the next succeeding bed.  The courses shall be laid truly and strictly to line and horizntal level.

f.   	Bond :

Brickwork courses shall be alternately laid in stretcher bond and header bond.  Damaged bricks shall not be used.  The greatest care shall be taken to prevent mortar dropping on to or in any other way disfiguring or discoloring the bricks, and all edges and sides shall be kept strictly  plumb and square, in-line, and flush with the required finished face.  As the work proceeds, it shall be continuously checked with a 2 m long straight edge and spirit level.

g.  	Construction :

Walls shall be carried up in a uniform manner and no one portion raised more than 1 m above another at any one time, the open end being racked out.  Over-hang work shall in no case be permitted.  Brickwork shall be cleaned down after each day’s work and newly laid brickwork shall be protected by suitable means.

h.  	Dry Weather :

In dry weather the suction rate of clay bricks shall be adjusted by wetting as necessary before use.  Bricks shall be stored in a free draining area and protected from rain.

i.  	Lintels :

Where brickwork rests upon lintels or supporting ribs of concrete, the bricks shall be cut as necessary and carefully bedded so that proper support to the outer leaf of brickwork is obtained.

j.  	Pointing :

At the time of laying, all joint of exposed brickwork shall normally be raked out neatly and pointed to 15mm depth.

k.  	Approval :

All workmanship shall be strictly in accordance with the foregoing.  The Engineer or the Engineer’s representative reserves the right to reject any of the work ongrounds of shabby workmanship.  Such rejected work shall be removed and rebuilt to the Engineer’s satisfaction.

l. 	Quantity of Mortar :

Quantity of mortar to be used in one Cum. of masonry shall vary from 0.30 Cum. for thin masonry to 0.32 Cum. for massive masonry of conventional bricks (second class).

m. 	Cement Mortar :

The cement mortar to be used on the work should be generally conform to specification No.13 of TNBP.  Only sufficient mortar shall be mixed as required for immediate use.  Partly set mortar shall not be used.

2.	Aggregates:

2.1	Sand for use in masonry  and plaster works shall confirm to relevant specification in TNBP (specification No.7) and I.S.2116/ 1985, I.S.1542/ 1977.

2.2	The coarse and fine aggregates for concrete shall conform to I.S.383/ 1970 and as specified in the relevant clauses of I.S.456/ 1978 .  Other aggregates free from deleterious materials shall be used at the concurrence and approval of the Engineer after sufficient tests have been carried out at the contractor’s cost.

  - The maximum quantities of deleterious materials in the aggregates, as determined in accordance with  I.S.2386 (Part II)/ 1963 shall not  exceed  the limits given in table I of  I.S.383.   Unless  otherwise  specified  all coarse aggregate in RCC shall be  graded aggregate of 20mm nominal size.   All aggregates shall be stored in hard impervious  surface  to ensure exclusion of all foreign materials and as per IS 4082/	1977 and specification no. 5 of TNBP volume I.

  - Aggregate having a specific gravity below 2.6 (saturated surface dry basis) shall not be used without the special permission of the Engineer.

3.	Water required for Construction:

3.1	The water used in the construction shall be of potable quality and shall be tested at the contractor’s cost. The  contractor has to make his own arrangements at his cost for water required for construction, testing, filling, etc., either from local bodies  or from elsewhere, by  paying the charges directly and arranging tanker etc., as per necessity. No claim for extra payment on account of non availability of water nearby or extra lead for bringing  water shall  be entertained.  All required piping arrangements and pumping  if required for water shall be made by the contractor at his cost. Water for mortar, mixing and  curing of concrete shall be free from harmful matter or other substances  that  may be  deleterious to concrete or steel and taken from a source 	approved by the Engineer.  Ground water for mixing and curing  shall conform to the provisions in the class 4.3  of  IS 456/ 2000.

4.	Admixtures:

Only  where a beneficial effect is produced shall any admixture be used and that  too after test has been carried out to convince the Engineer that no harmful effect will be produced by the use of such admixture  and after approval by the Engineer. The admixture shall conform to IS 9103/ 1972

5. 	Form Work and Centering

5.1	Steel/ wooden form centering shall be used. If wooden form work is used, it shall  consist of planks not less than 40mm thick and strong props.  This shall be provided complying with clause 10  of IS 456/ 2000 and  specification no.30.8 of TNBP.  The timber for form works shall be best hard wood and got approved by the Engineer. This shall be deemed to be included in the items of contract even otherwise specified.

6.	Separator ( Cover Block )

6.1	For  bottom cover of beams, slabs etc., separators  of pre cast  cement mortar blocks of suitable size with wire embedment as directed  shall be used and tied to the reinforcement. Between layers of reinforcements, separators consisting of pieces of bars of suitable  diameter shall be used .  The  required cover shall be provided as per clause 24-4 of IS 456/ 2000.

7.	Pipes , Specials and Valves

7.1	General

7.1.1	All types of pipes required for the works should be of good quality conforming to relevant BIS and should be procured from reputed manufacturer or his authorised dealer.  Each pipe should bear the trade mark of the manufacturer, the nominal diameter, class, weight, batch number and the last two digits of the year of manufacture suitably and legibly marked on it.  The Engineer shall have the right to conduct any test to ascertain the quality of the pipes supplied by the contractor. The contractor should make all necessary arrangements for testing the pipes.  The cost of such test shall be borne by the contractor.

The materials which are classified for ISI marking should be supplied with ISI marking only.

7.1.2	If on examination of any sample from any portion of the supply, the material is found to be sub standard and not fully in accordance with the relevant specification, the entire consignment shall be rejected.  In case of doubt whether the materials conform to the specification or not, the decision of the Executive Engineer shall be final.

7.2.  Stoneware pipes

7.2.1.  	The stoneware pipes shall strictly conform to IS 651/ 1992 and as amended from time to time.

7.2.2.	The contractor should procure the stoneware pipes from a reputed manufacturer.

7.2.3.	The contractor should furnish the test certificate issued by the manufacturer.

7.2.4.	The manufacturer’s test certificate and third party inspection certificate should be produced by the contractor for the pipes used in the works.

7.2.5.	 In addition to third party inspection, wherever felt necessary, the Engineer shall have the power to test the stoneware pipes for its quality such as internal hydraulic pressure test, diameter, thickness, crushing strength etc. in TWAD Board laboratory.

7.3 	DWC pipes:

DWC structured well Polyethylene piping system (Pipe with online/offline coupler and Elastometric sealing ring) with required specials non smooth external uannural corrugated and smooth internal surface – Double wall SN 8 Class non pressure UGSS application as per IS-16098 (Part-2) 2013/ EN: 13476-3 (latest revision) including elastomeric sealing ring gasket suitable for DWC pipes conforming to IS: 5382 (latest revision) Type-B Pipes of size 150mm to 300mm shall be used for sewer lines with Elastometric rubber O ring as jointing material for the depth upto 3 m.

7.3.1.1	Specification for High Alumina Cement Lined RCC Pipes:

The main purpose of using High Alumina Cement for lining is to protect the pipe against sulfate attacks when it is used in sewer lines.  All reinforced concrete pipes shall be of spun concrete and lined with a 12 mm thick High Alumina lining.

The normal proportion of the mix shall be as follows:

i.	High Alumina Cement one part – as per IS:6452.

ii.	Granite dust passing through IS sieve 150 micron – one part

iii.	Fine aggregate passing through IUS sieve 1.18 mm as per IS 383.

iv.	Water cement ratio of the lining mix shall not be more than 0.35 and shall be sufficient to ensure maximum density.

7.3.1.2	 Process of manufacture

The pipes shall be made by spinning process.  The centrifugal force generated by spinning action will force the concrete against the mould, removing excess resulting in a dense concrete.  The mix for high alumina cement lining shall be mixed in small separation mixer.  All the ingredients shall be weighed.  As soon as the spinning pipe is completed, the cement mortar shall be fed into the rotating mould uniformly and the pipe shall be spun until the cement mortar is set.

7.3.1.3	Precaution to be taken for high alumina lining

i.	It is not desirable to mix and do the lining in high constant temperature (temperatures more than 40o c)

ii.	Steam curing should not be used for curing pipes.

iii.	The high alumina lining shall be kept moist and cool for the first 24 hours.  The curing of lining shall be started after 3 to 4 hours after operation.

iv.	The water cement ratio of the lining shall not be more than 0.35

7.3.1.4	Socket and Spigot

The outside of the spigot portion of the pipe shall be coated with epoxy coating and poly solution coating inside the socket portion shall be made before lowering into the trenches.

7.4.   	UPVC  pipes

The UPVC pipes should be as per IS 15328:2003 and amended from time to time. The UPVC pipes joints shall be with solvent cement of good quality, conforming to IS    IS 15328:2003. the pipes are as per BIS, by visual examination, diameter, weight, wall thickness, flexibility, colour etc.,

7.5. 	Cast Iron pipe and fittings:

Cast iron pipe of LA clause shall conform to IS:1536 and fittings as per IS:1538 and laying shall be as per IS:3114.  The test procedure, the scale of sampling and the criteria for acceptance of rubber rings shall be as per IS 5382 and IS 3400 in case of rubber ring joints.

The spigot socket joints shall be with tyton joints with rubber gaskets.    The CI flanged pipes and specials shall confirm to IS 1538. After laying and jointing of CI pipes and fittings the pipe line shall be tested at work site in suitable stretches before back filling excavated earth, as per specifications.

7.5	Valves

7.5.1	The contractor should  procure reputed make of sluice valves, scour valves, reflux 	valves and air valves from the manufacturer or his authorised dealer and they should conform to the relevant BIS specification and suitable for use in the work.  The valves shall bear ISI marks.

7.6	CI/ PVC/ Specials and Fittings

7.61	The specials and fittings should be in conformity to the relevant BIS specification

7.7	Testing of Pipes

7.7.1	The third party inspection certificate should be produced by the contractor for the pipes used in the work. It is mandatory supplied at site Batch/Consignmentwise have to be tested at TWAD Laboratory as per the procedure annexed.  The engineer shall have the right to test the pipes, wherever felt necessary for its quality.  The cost of tests shall be borne by the contractor.

7.7.2	Testing of materials to be used in works, for the quality of finished items shall generally be done by the contractor and The cost of such test shall be borne by the contractor.

III .  CIVIL WORKS.

- General.

  - Tamil nadu Building Practice (TNBP) shall be strictly followed for carrying out different items of the work for which no standard specifications are available and no alternate specification have been given  under the description of works.

  - Where any provision of the TNBP is repugnant to or at variance with any provision under BIS or description of work, technical specifications and conditions  of contract, the provisions of the later shall be deemed to supercede the provision of the TNBP.

- Earth work.

  - Specification.

Tamilnadu  Detailed Building Practice (specification No.23 to the extent applicable)shall be followed for earthwork excavation.

  - Conveyance.

The excavated earth, blasted rubble etc., shall be conveyed and deposited in the departmental lands within 150m of plant site and as directed by the Engineer.

  - Stacking.

Where the location of the work is such and does not permit the deposition of excavated earth while digging trenches for laying pipes, the excavated earth should be conveyed to a convenient place and deposited there temporarily, as directed by the Engineer.  Such deposited soil shall be reconveyed to the site of work for the purpose of refilling of trenches, if it is suitable for refilling.  The unit rate for trench work of excavated and refilling shall include the cost of such operation.

2,4. Disposal of surplus Earth.

The excavated soil which is surplus to that required for filling and after allowing for settlement will have to be removed, spread and sectioned at places shown on the site  during  excavation for purpose of widening or levelling the road.  Sectioning is to be done as detailed in TNBP, It is to be understood that no extra payment, will be  made for t his and the unit rate for trench work of excavation and refilling shall made for this and the unit rate for trench work of excavation and refilling shall include the cost removal of surplus earth  to disposal site approved by the Engineer, its  spreading and sectioning at the bidder’s  expense.

2.5   	Shoring, Strutting and Baling out water.

The rate for excavation  of trench work shall include charges of shoring, strutting, bailing out water wherever necessary and no extra payment will be made for any of these contingent works.  While baling out water, care should be taken to see that     the bailed out water is  properly channelised to flow away without stagnation or inundating the adjoining road surfaces and properties.

- Concrete.

  - Specification.

Concrete for use in the works shall generally comply with TNBP (specification No.30)and the relevant BIS.  The concrete mix shall be in specified proportions satisfying the maximum aggregate size, water cement ratio and required cube strength and workability as per IS 456- 2000.  Such concrete  must be adequately  vibrated to form solid mass without voids.  The entire concreting works should be done only with the prior approval and in the presence of Engineer.

  - Mixing Concrete.

The concrete shall be proportioned as far as cement and aggregates are considered by volume.  The amount of water required being measured either by weight or volume the adjustments must be made to frequent intervals at the discretion of the Engineer or his assistant to account for the moisture content of the aggregates.  The mixing operation shall be performed only in a mechanical concrete mixer and shall continue until the whole batch of uniform consistency and colour.  The mixing of concrete shall be done in accordance with clause 8 and 9 of IS 456-2000.

  - Transporting, Placing and Compacting Concrete.

    - Transportation, placing and compaction of concrete mix  by mechanical vibrators shall be done in accordance with clause 12 of IS 456-2000.  It is imperative that all concreting operations be done rapidly and efficiently with minimum rehandling and adequate manpower shall  therefore be employed to ensure this.

    - The forms shall be first  cleaned and moistened before placing concrete.

    - The mix should not be dropped from such a height as it may cause segregation and air entrainment.  When the mix is placed in position, no further water shall be added to provided easier workability.

    - No concrete mix shall be used for the work if it has been left for a period exceeding its initial setting time before being deposited and vibrated into its final position in the member.

    - While one concrete is being placed in position it shall be immediately spreaded and ramped sufficiently and suitable to attain dense and complete filling of all spaces between and around the reinforcement and in to the corners of form work for ensuring a solid mass entirely free from voids.

    - Construction joints required in any of the structural members shall be provided generally complying with clause 12.4 of IS 456 - 2000 and as directed by the Engineer. The efficiency of tempering and consolidation will be judged by complete absence of air pockets, voids and honey combing after removal of form works.

3.4     Curing.

    - Curing shall be done to avoid excess shrinkage or harmful  effort  to the members generally  complying with clause 12.5 of IS 456 - 2000

    - The method adopted shall be effective and  any special  method used must be approved by the Engineer and be subject to complete supervision.

    - Any deficiency in concreting such as cracking, excessive honey combing exposure of reinforcement or other fault which entail replacement of the defective part by fresh concrete and whatsoever remedy reasonable required  without hampering the structural safety and architectural concept, all at the cost of contractor.

.

  - Removal of Form Work.

3,5,1.   Removal of form work shall be done as per TNBP and BIS and as directed by the engineer in such a manner that no damage is caused to the structures.  The striping time shall not be less than that indicated in clause 10.3 of IS 456 -2000.

  - Testing of Concrete

During the course of construction works, preparation of test specimens, curing and casting of concrete shall be done in accordance with IS  1199 / 1959 and IS 516 / 1959 to ascertain the  strength requirements and acceptance criteria indicated in IS 456 - 2000.  The contractor shall provide all apparatus, labour and arrange to test the cubes at TWAD Board Laboratory. The cost of such test shall be borne by the contractor.

    - In addition to the above tests, any other test which may if desired by the Engineer be carried out from time to time as per relevant specifications at the cost of TWAD Board.  In case the concrete does ot meet the strength required, all corrective measures shall be taken at once at the contractor’s cost.

    - The inspection and testing of structures shall be done in accordance with clause 16 of IS 456/2000

- Masonry

  - All masonry works such as Random Rubble / Brick work  must be done as per TNBP Specification.

- Plastering.

  - Plastering would be 12mm, 20mm and 25mm thick cement plaster .either plain or waterproof as may be specified.

  - The plastering items shall be executed in thickness and cement mortar of proportion as detailed in respective items in the BOQ.  Similarly the plastering shall be either ordinary or waterproof as specified in respective item in the BOQ.

  - In case of water proof plaster standard approved water proofing compound shall be mixed in cement mortar in required percentage as directed and then the plaster  is applied.

  - The finishing shall be either smooth or rough as may be directed by the Engineer unless otherwise specifically mentioned in the BOQ.

  - Neat finish wherever directed by the Engineer shall be done at no extra cost.

  - Curing and watering shall be one as directed  and plaster shall be in alignment and level. Any sub standard work is liable to be rejected and shall have to be re-done at  contractors cost.  Sand to be used shall be of approved quality only. Cost of all scaffolding shall be included in  the  rates quoted  in the BOQ.

- Flooring.

6.1.         40mm thick cement concrete 1:2:4 shall be provided for flooring ,  The size of  metal shall not be more  than 12mm and it shall be properly graded. A thin  coat of   very fine plaster shall be provided  on top  to give a smooth finish.    The marking  of false grooves to surfaces as directed includes the cost of labour.

- Doors and Windows.

  - Sizes shown on drawings are clear openings in masonry and not the shutter's size.  These sizes shown on drawings are, therefore, inclusive of required frame sizes and doors  windows, etc., and shall be manufactured, accordingly .  If sizes bigger than shown in drawings are manufactured, as instructed specifically in writing they shall be measured and paid for accordingly.

  - The work shall be executed as per the size of frame thickness of shutter type  viz.  Plain planked panelled, glazed etc., and fixture, etc., as described in Bid item.  Iron  bars for windows and ventilators  are to be provided if specifically mentioned in the bid item at Contractor's cost.  Specifications in TNBP shall be applicable.

  - The design of shutters and quality of wood shall be got approved form the Engineer  before manufacture.  The CW/TW to be used for wood work shall be uniform in substance straight, free from  large deed knots, flows flanks.  The work shall be done as per   specification  of TNBP latest edition.  The joints shall be perfect.

  - Part of wood embedded in masonry shall be painted with the tar.  The frames of doors, windows, ventilators, etc., shall have proper hold -fasts embedded in masonry.

7.5.            Whenever iron bar is to be provided as per   bid item  the rate  thereof is included in bid item.  The painting shall be done as prescribed in bid item.  No painting, however, shall be permitted till the wood work is approved by the Engineer.

  - Any substandard work not conforming to the specifications are liable to be outright  rejected and Executive Engineer's decision in such case shall be final and binding on the Contractor.

  - The mode of measurement shall be on area units as mentioned in BOQ.

- Painting.

8.1.          The work shall be carried out as per the description of the bid item and as directed    by Engineer.  It  shall be white washing, distempering and/or snowcem painting.  Shade and make shall be  as  directed by the Engineer and for decorative purpose.  Engineer may ask  for different shades to be provided for different components or different parts of the same component which the Contractor shall have to do within his bid rate only at no extra cost to  the Employer.  Cost  of priming coat as directed, scaffolding etc., shall be included in the bid rate.  The work shall be executed as per the specifications of TNBP for painting.

In general, all items of works must be done as per TNBP specifications and bid schedule specifications.

IV. SPECIAL SPECIFICATION FOR SEWERAGE WORKS

1.      	Sight rails and Boning rods

  - The works will be set out by the Contractor. The Contractor shall be required to fix over the centre of each machine-hole or where a change in direction or gradient occurs a strong timber sight rail, 150mm x 25mm with top edge placed straight and true. These shall be supported and fixed to stout wooden posts at each side of the excavation. The centre line of the sewer shall be marked on each sight rail both back and front by a single vertical line drawn thereon and on other side white. All lengths of sewer shall have three sight rails fixed one at each end and one in the centre and worked one with the other. The boning rods shall have a movable cross head at right angles to the rod. So arranged that it can slide up and down the rod and capable of being fixed at any required position on the rod by screws. The foot of the boning rod shall be provided with the shoe made truly at right angles to the rod so that when placed on the pipe being laid it shall rest properly on the pipe when the rod is truly vertical.

- Brick Machine-holes

  - Machine-holes shall be constructed on the sewers in the positions shown in the drawings. The work shall be done strictly in accordance with the detailed drawings except where alterations are required by the Engineer. The excavation shall not be larger that sufficient to admit of the trench being properly timbered and to facilitate plastering outside. The bottom of the excavation shall be properly leveled up, rammed and a bed of concrete laid thereon. When the concrete has sufficiently set the construction of the brick walls shall then be proceeded with all stoneware pipe connections through the walls shall be made and all iron work fixed in as constructions proceeds. Machine-hole less than 2.5m from invert to sewer to ground level shall be built rectangular and shall have a flat top constructed as shown in the drawings, Machine-holes more than 2.5m from surface to invert shall be built circular and the walls corbelled as shown in the drawing.  The inside of all machine-holes shall be plastered with cement mortar 1:3 20mm thick  and out side of all machine-holes with cement mortar 1:5 12mm thick. The machine-holes bottoms shall be properly formed with stone ware channels fixed in cement mortar. The channels shall be neatly formed to the radious of the pipe and all side connection curved and channeled to admit the sewage to entire at an angles of 45 degree to the line of flow Machine-holes shall be topped with a circular cast iron frame with cover or cover of such pattern as may be ordered by the Engineer. The machine-hole frame shall be fixed to the top of the brick work by a layer of cement mortar.

  - Where pipes pass through walls of machine-holes relieving arches shall be turned neatly over the upper half of the pipes. If any pipe enters at such an angle that a relieving arch cannot be properly turned the bricks shall be carefully cut and laid so as to fit closely and neatly against the pipe, and a RCC lintel shall be provided to avoid load of the walls being transmitted to the pipes.

  - The stoneware drop pipe connection in machine-holes shall be secured to the wall of the machine-holes by suitable clamps and shall be built in as the work proceeds in accordance with the drawings and the above instructions.

  - Cast Iron steps shall be built in each machine-hole as the work proceed one being inserted to every four courses of brick work, horizontal distance centre to centre of each row being 30cm

  - The Contractor shall include in his prices for completing all machine-holes in accordance with the drawings.

- RCC   Machine-holes

  - Machine-holes shall be constructed on the sewers in the positions shown in the drawings or in such position as the Engineer may direct. The work shall be done strictly in accordance with the detailed drawings except where alterations are required by the Engineer. The excavation shall not be larger that sufficient to admit of the trench being properly timbered and to facilitate eash work. The bottom of the excavation shall be properly leveled up, rammed and a bed of concrete laid thereon. When the concrete has sufficiently set the construction of the RCC walls shall then be proceeded with and all stoneware pipe connections through the walls shall be made and all iron work fixed in as constructions proceeds. The machine-holes bottoms shall be properly formed with stone ware channels fixed in cement mortar. The channels shall be neatly formed to the radious of the pipe and all side connection curved and channeled to admit the sewage to entire at an angles of 45 degree to the line of flow Machine-holes shall be topped with a circular cast iron frame with cover or cover of such pattern as may be ordered by the Engineer. The machine-hole frame shall be fixed to the top of the brick work by a layer of cement mortar.

  - Where pipes pass through walls of machine-holes relieving arches shall be turned neatly over the upper half of the pipes. If any pipe enters at such an angle that a relieving arch cannot be properly turned the bricks shall be carefully cut and laid so as to fit closely and neatly against the pipes.

  - The stoneware drop pipe connection in machine-holes shall be secured to the wall of the machine-holes by suitable clamps and shall be built in as the work proceeds in accordance with the drawings and the above instructions. The cost of this work will be paid separately.

  - PVC encabsulated  steps shall be built in each machine-hole, horizontal distance centre to centre of each row being 30cm.

  - The Contractor shall include in his prices for completing all machine-holes in accordance with the drawings.

- Cleaning out Sewers and Machine-holes

During the whole of the work the contractor shall keep interior surface of sewers and machine-holes free from cement mortar, bricks, soil or other superfluous matter and shall handover the sewers perfectly clean and free from deposit on completion.

- Water Test of Sewers

  - All sewers shall be tested before the filling in of the trench or other excavations. Testing shall also be done after refilling of the trench or other excavation, if considered necessary by the Engineer. The testing or retesting shall be carried out by and at the expenses of the Contractors who shall also provide the necessary appliances and water for the same. The tests will only be made from machine-hole to machine-hole after the machine-holes connected with the length under test have been completely finished.

  - The test shall be carried out in the following manner.

  - The pipes shall be carefully cleared of all earth or materials that may be lying thereon or therein and all joints shall be exposed right round so that through examinations may be made while the pipes are under test.

  - The ends of the pipe shall be closed by means of expanding stoppers and all junctions with stoneware stoppers or cement disc fixed in cement mortar.

  - The last but one pipe at the higher end of the length shall be a junction pipe with the junction arm at the top which will permit of the filling of length with water and also allow the escape of all air in the pipes.

  - The expanding stoppers at each end of the length under test shall have a hold in the centre with a small piece of a pipe screwed therein and threaded on the projecting piece to permit of a flexible tube not less than 2m long fixed there to by a coupling. At the end of the tubing, the following shall be fixed.

- at lower end of length, a sock.

- at top end of length, a funnel of 15cm diameter.

  - The top of the funnel shall be fixed rigidly at a height of 30cm above the ground level, or such other height as may be decided by the Engineer.

  - After the above-mentioned expanding stoppers have been fixed together with flexible tubing and funnel, the length shall then be filled with water through the junction arm of the pipe provided therefore. As soon as the water has risen of the level of the filling junction arm an expanding stopper shall be fixed thereon. After a short time has been allowed for absorption, water shall be poured into the funnel until the same is filled to the top.

  - If any of joints are leaking or if during a period of ten minutes the water level in the funnel drops 25mm or more (no more water being added or sewer interfered with in any way during the period) the test shall be considered unsatisfactory. If the water does not drop more than 25mm and there is no sign of leakage at any of the joints, the test shall be continued for one hour and at the end of the hour the pipe lines including the joints shall be examined and, if no indication of sweating or leakage is found then the test will be considered satisfactory. Should the test be unsatisfactory, all such joints or pipes found to be defective shall be removed, replaced or re-laid to the satisfaction of the Engineer by the Contractor at his cost.

  - The test shall be done as many times as may be necessary until the length is found to be watertight to the satisfaction of the Engineer.

  - The water required for testing shall be clean.

- Materials:

  - Salt glazed stoneware pipes:

The stoneware pipe to be used shall be of the approved make and shall conform to IS:651-1980.  All pipes shall be perfectly straight and truly cylindrical, glazed inside and outside, free from cracks and flaws, and perfectly burnt.  Those not conforming to above mentioned requirements shall be rejected.  The pipes used in the project shall be of  200mm, 250mm & 300mm.

  - DWC pipes:

DWC structured well Polyethylene piping system (Pipe with online/offline coupler and Elastometric sealing ring) with required specials non smooth external uannural corrugated and smooth internal surface – Double wall SN 8 Class non pressure UGSS application as per IS-16098 (Part-II) Type-B Pipes of size 150mm to 300mm shall be used for sewer lines with Elastometric rubber O ring as jointing material for the depth upto 3 m.

  - Cast Iron pipe and fittings:

Cast iron pipe of LA clause shall conform to IS:1536 and fittings as per IS:1538 and laying shall be as per IS:3114.  The test procedure, the scale of sampling and the criteria for acceptance of rubber rings shall be as per IS 5382 and IS 3400 in case of rubber ring joints. CI pipes of sizes from 150mm dia shall be used for Pumping main, Sewer main.

  - UPVC  pipes

UPVC pipe confirm to IS 12818/2003  should have almost inert to corrosion and chemical reaction.  Hence, it can be used in salty, sandy and chemically aggressive water, without creating problems latter on.  UPVC  Pipes of size  110 mm dia shall be used for House Service Connection and narrow street.,

  - Machine-hole-frames & cover:

The machine-hole frames & covers shall be of fibre reinforced concrete with clear opening of 600mm diameter pipe & of heavy duty type to withstand heavy load of traffic (i.e IRC class AA load).  The machine-hole frame & cover shall conform to IS.12592 part I of 1982. It shall be inspected before supply by the Engineer.

  - Machine-hole steps:

The footrest or steps for entry into the machine-hole or flush tank shall be of plastic encapsulated steps instead of Cast iron steps generally used.  The plastic encapsulated steps shall be of 3mm thick plastic encapsulated as per IS - 10910 on 12mm dia steel bar as per IS - 1786 having minimum cross section as 23 x 25mm and overall minimum length 263mm and width as 165mm with minimum 112mm space between protruded legs having 2mm tread on top surface by ribbing or chequering besides necessary and adequate anchoring / projection on tail length of 138 mm and suitable to withstand the bend test, twist test, plastic integrity test and chemical resistance test as per detailed specification.  The machine-hole steps shall be inspected before supply by the Engineer.

7.   	Carting & Handling of pipes / specials:

Pipes and fittings / specials shall be transported from the factory to the work sites as directed by owner / engineer.  Contractor shall be responsible for the safety of pipes and fittings / specials in transit, loading / unloading.  Every care shall be exercised in handling pipes and fittings / specials to avoid damage.  While unloading, the pipes and fittings / specials shall not be thrown down from the truck on to hard surfaces.  They should be unloaded on timber skids with steadying ropes or by any other approved means.  Padding shall be provided between coated pipes, fittings / specials and timber skids to avoid damage to the coating.  Suitable gaps between pipes should be left at intervals in order to permit access from one side to the other.  In case of spigot socket pipes, care should be taken regarding orientation of pipes while unloading.  As far as possible pipes shall be unloaded on one side of the trench only.  The pipes shall be checked for any visible damage (such as broken edges, cracking or spalling of pipe) while unloading and shall be sorted out for reclamation.  Any pipe which shows sufficient damage shall be prohibited.

8.  	Storage of pipes:

Each stack of pipes shall contain only pipes of same class and size, with consignment or batch number marked on it with particular of supplier wherever possible.  Storage shall be done on firm level and clean ground and wedges shall be provided at the bottom layer to keep the stack stable.  The stack shall be in pyramid shape of the pipes laid lengthwise and crosswise in alternate layers.  The pyramid stack shall be made for smaller diameter pipes for conserving space in storing them.  The height of the stock shall not exceed 1.5m.  Fittings / specials shall be stacked under cover and separated from pipes.

Rubber rings shall be stored in a clean, cool place away from windows, boiler, electrical equipment and petrol, oils or other chemicals.  Particularly in the field where the rubber rings are being used it is desirable that they are not left out on the ground in the sun or over night under heavy frost or snow conditions.

- TRENCH EXCAVATION

9.1.   	General:

Trench excavation means excavation of trenches into which the pipe is to be laid.  The line and levels of trenches shall be as shown on the drawings or as may be directed by the Engineer.  Before commencing trench excavation, the route of the trenches shall be pegged out accurately and the natural ground levels shall be agreed with the Engineer.

9.2.  	Width of Trench:

The width of trench measured at the crown of the pipe shall permit adequate working space.  The trenches shall be widened at sockets and other structures as may be found necessary.  Payment for excavation shall be made on quantity basis as per actual dimensions of trench excavated subject to the condition that the quantity shall be limited as per the trench cross-section necessary to keep the trench in vertical position.

9.3.  	Depth of Excavation of Trenches:

The depths for the trenches will be calculated from the surface to the invert of the machine-holes for the pipes.  The trench shall be so dug that the pipe line may be laid to the required gradient between the adjacent machine-holes and to the required depth.  A minimum cover of 0.9 m is to be taken above the crown level of pipe upto the ground level / road level.

9.4. 	Barricading by Fencing, watering, lighting:

The parts of the fencing shall be of timber, securely fixed in the ground not more than 2.50 m. apart.  They shall not be less than 10cm in dia or not less than 1.25 m above the surface of the ground.  There shall be two rails, one near the top of the post and the other about 0.5m above the ground and each shall be of 5 cm to 10cm in diameter and sufficiently long to run from post to post to which they shall be tied with strong ropes.  The method of projecting rails beyond the posts and tying together where they meet will not be allowed on any account. All along the edges of the excavated trenches, a bund of earth about 1 m high shall be formed when so required by the Engineer for further projection.  Proper provision shall be made for lighting at night and watchman shall be kept to see that this is properly done and maintained.  In addition to the normal lighting arrangements the contractor shall provide, whenever such work is in progress, battery operated blinking lights (6 volts) in the beginning and end of a trench with a view to provide suitable indication to the vehicular traffic.  The contractor shall also provide a display special board printed with fluorescent prints indicating the progress of work along the road.  In the event of the contractor not complying with the provisions of the clause, they will be imposed fine which will be decided by the Engineer.  Further, in all such cases, the work may be carried out at the risk and cost of the contractor. The Contractor shall be held responsible for all claims for compensation as a result of accident or injury to persons during the course of execution of the project.

The contractor shall at his own cost provide all notice boards before opening of roads as directed by the Engineer.  Arrangements shall be made by the contractor to direct traffic when work is in progress.

9.5. 	Blasting for pipe laying:

In case of excavation in rock whether by chipping or chiseling in crowded localities or blasting using  explosives in other localities, pre measurement of the area to be removed shall be got approved by the engineer.  After the excavation is completed, the rocky material shall be stacked & got measured by the engineer, so that the removed & stacked material shall agree for the purpose of payment.

In case of refilling of the trench, where the pipe are to be laid in rocky strata, the pipe shall be laid true to line & gradient over proper bedding & while the sides & the top of the pipes shall be refilled with borrowed earth from adjoining areas or conveyed earth from other areas.  Blasted materials shall not be used for refilling the trenches.

9.6.  	Trench excavation in roads and footpaths:

All trench excavation and other work carried out within the limits of any road shall be completed as rapidly as possible and  not more than half of the width of the carriage way shall be obstructed at one time.  Road drains shall be kept free from obstruction.  In any event the Contractor shall take special precautions, which shall include the continuous support of the sides of the excavation, from the time when excavation is begun until the refilling of the trench in places, to ensure that there is no disturbance of the adjacent road or road foundation.

Where excavated material has temporarily been deposited on a grass margin or road pavement, the margin or road pavement shall on completion of refilling be restored entirely to its original condition to the satisfaction of the concerned department and left free from loose stones.

9.7.  	Trench excavation in fields:

The term "fields" includes fields, moorlands, grass verges and the like and all private lands, and no length of trench excavation located in fields shall be commenced until suitable temporary fencing has been erected around that length unless the Engineer permits otherwise.  Temporary fencing shall not be removed without the Engineer's permission, which will not normally be given until the Trench Excavation has been refilled and reinstated to the original ground condition or as directed by the Engineer.

The contractor shall have particular regard to the safety of livestock in fields or which may be introduced to the fields, and shall ensure that all open excavations, access routes and steep or loose slopes arising from the contractor's operations in these fields are adequately fenced and protected.

After the erection of temporary fencing the Contractor shall remove top soil to such depth and over such area as may be necessary to provide sufficient material to ensure adequate surface reinstatement of the working areas occupied by the contractor for construction of the pipe line.

9.8.  	Trench sides:

Loose boulders shall be removed from the sides of the trenches before allowing workmen into the excavation, and the trench sides shall be stabilized with screening or other methods approved by the Engineer.  Trench slopes shall be kept moist where necessary to prevent local sliding as ordered by the Engineer.

9.9.  	Timber shoring:

Shoring & strutting has to be done for the total depth of trench including the top 2m when the  depth of the trench exceeds 2m & above in loose soil.  Shoring & strutting has to be done for both sides of the trench.  However, when the depth is less than 2m shoring need not be done. Close timbering shall be done by completely covering the sides of the trenches and pits generally with short, upright members called 'rolling boards'.  The boards shall generally be placed in position vertically side by side without any gap on each side of the excavation and shall be secured by horizontal wallings of strong wood at maximum 1.2 metres spacings and suitably strutted.  If the soil is very soft and loose, the boards shall be placed horizontally against each side of the excavation and supported by vertical wallings, which in turn shall be suitably strutted.  The lowest boards supporting the sides shall be taken into the ground and the portion of the vertical side of the trench or pit shall remain exposed, so as to render the earth liable to slip out.

The shoring material shall not be of sizes less than those specified below unless steel sheet piling is used or unless otherwise approved by the Engineer in writing:

a)	Planks				-	5cm x 25cm

b)	Waling pieces			-	10cm x 20cm

c)	Struts				-	15cm x 20cm

Timber shoring shall be 'close' or 'open' type, depending on the nature of soil and the depth of pit or trench.  The type of timbering shall be as approved by Engineer.  It shall by the responsibility of the contractor to take all necessary steps to prevent the sides of excavations, trenches, pits, etc., from collapsing. In the case of open timbering, the entire surface of the sides of trench or pit is not required to be covered.  The vertical boards of minimum 25cm x 4cm sections shall be spaced sufficiently apart to leave unsupported strips of maximum 50cm average width.  The detailed arrangement, sizes of the timber and the spacings shall be subject to the approval of the Engineer.  In all other respects, the specification for close timbering shall apply to open timbering.

In case of large pits and open excavations, where shoring is required for securing safety of adjoining structures or for any other reasons and where the planking across sides of excavations / pits cannot be strutted against, suitable inclined struts supported on the excavated bed shall be provided.  Load from such struts shall be suitably distributed on the bed to ensure no yielding of the strut.

9.10. 	Inspection by engineer:

When the required levels of trench excavation are reached, the Engineer will inspect the ground exposed and if he considers that any part of the ground is by its nature unsuitable he may direct the Contractor to excavate further and to refill the further excavation with such material as he may direct.

Should the bottom of any trench excavation while acceptable to Engineer at the time of his inspection subsequently become unacceptable due to exposure to weather conditions or due to flooding or have become puddle soft or loose during the progress of the works the contractor shall remove such damaged, softened or loosened material and excavate further.

9.11.  	Disposing material from trench excavations:

The Contractor shall make his own arrangements for the temporary storage of any excavated material which is required for use in refilling trench excavations, including any necessary double handling.  Any excavated material not required for or not suitable for use as refilling shall be removed.

9.12.  	Trenches not to be left open:

Trench excavations shall be carried out expeditiously and, subject to any specific requirements of the contract, the refilling and surface restoration of trench excavations shall be commenced and completed as soon as reasonably practicable after the pipes have been laid and joined.

9.13.  	Refilling trenches:

With a view to restrict the length of open trenches, on completion of the pipe laying operations, refilling of trenches shall be started immediately by the contractor.  Pipe laying and testing shall follow closely upon the progress of trench excavation and the contractor shall not permit unreasonable excessive lengths of trench excavation to remain open while awaiting testing of the pipe line.

The trench shall be filled with excavated material above the top of pipe, back filling is to be done keeping at least 90 cm length of pipe open at the joints, for verification of joints for water tightness during testing.

Care shall be taken while back filling, not to injure or disturb the pipe.  Filling shall be carried out simultaneously on both the sides of the pipes so that unequal pressure does not occur.  Walking or working on the completed pipelines shall not be permitted unless the trench has been filled to a height of at least 30cms over the top of the pipe except as may be necessary for tamping etc. during back filling work.

Filling-in shall be done in layers not exceeding 150mm in thickness accompanied by adequate watering, ramming etc. so as to get good compaction.  The trench shall be refilled so as to build upto the original ground level, keeping due allowance for subsequent settlement likely to take place.  Before and during the back filling of the trench, precautions shall be taken against the floatation of the pipeline due to the entry of large quantities of water into the trench causing an uplift of the empty or the partly filled pipeline.

10. 	Measurement:

The laying of sewers (RCC / stoneware) shall be measured from inside of the first machine-hole to the inside of the adjoining machine-hole.  The machine-hole are measured from the invert of the machine-hole to the ground level as the depth of machine-hole.

11.	SEWER APPURTENANCES:

Brick Machine-holes:

Machine-holes shall be constructed on the sewers in the positions shown in the drawings or in such position as the engineer may direct. The work shall be done strictly in accordance with the detailed drawings except where alterations are required by the engineer. Any variation in locating the machine-holes and subsequent revision in levels during execution if found necessary, shall be carried out by the bidder at his cost. The excavation shall not be larger than sufficient to admit the trench being properly timbered and to facilitate plastering outside. The bottom of the excavation shall be properly levelled up, rammed and a bed of concrete laid thereon. When the concrete has sufficiently set all stoneware pipe connections through the walls shall be made and all ironwork fixed in as constructions proceeds.  Machine-holes upto 2.5m from invert of sewer to ground level shall be built rectangular and shall have a flat top constructed as shown in the drawings, machine-holes more than 2.5m from surface to invert shall be built circular and the walls corbelled as shown in the drawings.  Machine-holes shall be constructed of 1st class bricks.  The inside of all machine-holes shall be plastered with cement mortar 1:3, 20mm thick and the outside of all machine-holes with cement mortar 1:5, 12mm thick.  The machine-hole bottoms shall be properly formed with channels fixed in cement mortar.  The channels shall be neatly formed to the radius of the pipe and all side connection curved and channeled to admit the sewage to enter at an angle of 45 degree to the line of flow.  Machine-holes shall be topped with a circular FRC frame cover conforming to IS 12592 part 1, heavy duty 600mm dia.  The machine-hole frame shall be fixed to the top of the brickwork by a layer of cement mortar.

Where pipes pass through walls of machine-holes relieving arches shall be turned neatly over the upper half of the pipes.  If any pipe enters at such an angle that a relieving arch cannot be properly turned the bricks shall be carefully cut and laid so as to fit closely and neatly against the pipe and a R.C.C. lintel shall be provided to avoid load of the walls being transmitted to the pipes.

Plastic encapsulated steps shall be built in each machine-hole as the work proceeds one being inserted to every four courses of brick work, horizontal distance centre to centre of each row being 300mm.  The contractor shall include in his prices for completing all machine-holes in accordance with the drawings.

RCC Machine-holes:

Machine-holes shall be constructed on the sewers in the positions shown in the drawings or in such position as the engineer may direct. The work shall be done strictly in accordance with the detailed drawings except where alterations are required by the engineer. Any variation in locating the machine-holes and subsequent revision in levels during execution if found necessary, shall be carried out by the bidder at his cost. The excavation shall not be larger than sufficient to admit the trench being properly timbered and to facilitate easy work. The bottom of the excavation shall be properly levelled up, rammed and a bed of concrete laid thereon. When the concrete has sufficiently set all stoneware pipe connections through the walls shall be made and all ironwork fixed in as constructions proceeds.  The machine-hole bottoms shall be properly formed with channels fixed in cement mortar.  The channels shall be neatly formed to the radius of the pipe and all side connection curved and channeled to admit the sewage to enter at an angle of 45 degree to the line of flow.  Machine-holes shall be topped with a circular FRC frame cover conforming to IS 12592 part 1, heavy duty 600mm dia.  The machine-hole frame shall be fixed to the top of the brickwork by a layer of cement mortar.

Where pipes pass through walls of machine-holes relieving arches shall be turned neatly over the upper half of the pipes.  If any pipe enters at such an angle that a relieving arch cannot be properly turned the spot shall be carefully cut and laid so as to fit closely and neatly against the pipe and a R.C.C. lintel shall be provided to avoid load of the walls being transmitted to the pipes.

Plastic encapsulated steps shall be built in each machine-hole as the work proceeds. The horizontal distance centre to centre of each row being 300mm.  The contractor shall include in his prices for completing all machine-holes in accordance with the drawings.

Drop machine-holes:

Wherever the drop depth for sewer line exceeds 0.60m drop machine-holes are provided.  Drop machine-hole shall be constructed on the sewers in the position shown in the drawings or in such position as the engineer may direct. The work shall be done strictly in accordance with the detailed specification / drawings except where alterations are required by the engineer. The stoneware drop pipe connection in machine-holes shall be secured to the wall of the machine-holes by suitable clamps and shall be built in as the work proceeds in accordance with the drawings.

Any variation in locating the drop machine-holes and subsequent revision in levels during execution if found necessary, shall be carried out by the bidder at his cost

# V. PIPE LAYING  WORKS

- General

  - The earthwork for the pipe laying work shall generally conform to the invert level given in the drawing

  - Wherever necessary, Granular bedding shall be given as per IS Standards and as directed by the Engineer.  The pipe should be laid true to the alignment line and grade Wherever necessary, appropriate bends should be used. The   pipes laid must be jointed properly and carefully by using approved type of jointing materials.

  - After the pipes are laid and jointed, the pipelines are to be subjected to hydraulic pressure test as detailed in the relevant BIS Specification for various types as indicated below.

In portion of pipeline, where the pipes have developed cracks or sweating, such pipes with jointing materials shall be removed and re laid with new pipes at the contractor’s cost and the pipe line shall be re tested to the entire satisfaction of the Engineer.  No extra payment will be made on this account.  The bidder has to make his own arrangements for the procurement  of the required equipments for testing of pipes which shall be subjected to such test as the Engineer deems fit to ensure the accuracy of the gauge.

  - Refilling shall be done with proper compaction with excavated earth.  In no case the contractor shall be allowed to refill the trenches in hard excavated portion to be refilled by the boulders or excavated stuffs.  This portion of trench shall be refilled by the soft strata from excavated stuff from distance place at no extra cost.  The refilling shall be done in 15 cm thick layers duly watering and compacting each layer.  The refilling may be done up to a height of 20 to 30 cm than the natural ground level to allow that sinking afterwards.  If the refilling gets sunk below the natural ground level at anytime till the completion of the work, the contractor at his cost should make good the refilling to the required level as may be directed by the Engineer.

  - In case of pipe trenches, the Engineer may reduce the width of trench wherever a hard strata is met with, if he feels adequate and just sufficient to lay the pipe line in order to reduce the hard rock quantity.  In such case the contractor will be paid as per the actual measurement.

  - If the work is in a residential area, the contractor should carry out the excavation carefully to avoid collapse of any structure.

  - Valves shall be provided with valve pits with proper cover to bear the loads coming on it as per bid documents and departmental drawings and specification.

  - Adequate protective measures should be taken against surge pressure.  Zero velocity valves and air cushion valves should be provided at the appropriate places Thrust blocks and anchor blocks should be provided at all bends and appropriate places.

  - Water required for testing  the pipeline shall be arranged by the contractor at his cost.

1.10  GRB BEDDING :  Granular bedding with graded hard broken stone of 20mm, 10mm  & 6mm in the ratio of 2:1.5:1, laying in layers of 15cm  thick including cost of materials and labour charges for        spreading, ramming & consolidation for pipe bedding

- Laying and jointing of stoneware pipe not on concrete

  - Before laying the pipes, the Contractor shall carefully brush them to remove any soil, stones or other materials which may be therein, even and regular bed having been prepared, and joint pit excavated to form a recess under the socket of each pipe of no greater width and depth than to enable the pipe jointing to be properly done. each pipe shall then be carefully lowered and placed singly in the trench and shall rest on the solid ground for a distance of not less than two thirds of its entire length.

  - Each pipe shall be brought into a true line from machine-hole to machine-hole, for this purpose, a strong twin line (rat thread) sufficiently long to reach the full length between machine-holes shall be used. Each pipe shall be set correctly to level by means of the boning rod and sight rails.

  - The spigot of each pipe shall be carefully wrapped with a ring a spun yam dipped in cement grout or tarred gasket sufficiently thick to properly fit me socket of the adjoining pipe and to allow true alignment. The Pipe shall then be driven fully home into the socket of the adjacent previously laid pipe and yam or tarred gasket carefully driven home with caulking tool.

  - The remaining space in the socket shall than be tightly and completely filled with cement mortar composed of one part of Portland cement and one and a half parts sand and shall be neatly beveled off alround the circumstances and finished at an angle of 45 degree outside the socket of the pipes. A wooden caulking tool shall be used for forcing the mortar into the sockets.

  - A tightly fitting bag of shavings or straw having a rope attached shall be drawn through the pipes as the work proceed to ensure that there is no cement or yam or other obstruction projecting into the interior.

  - All joints shall be kept moist either by means of wet bags, wet clay or wet earth which ever may be ordered bv the engineer to protect them from the sun. Such covering shall be removed when the length in tested for water thightness.

3. Laying stoneware pipes on Concrete

3.1 	In trench where ordinary socket and spigot stoneware pipes are to be laid on concrete bed, the method to be adopted is as follows,

  - When the earth is taken out to the proper depth and gradient, a concrete bed of suitable thickness and width is to be laid as directed by the Engineer. The top of this concrete bed shall also be to the required gradient

.

  - When the concrete has set sufficiently, a series of special concrete invert blocks are to be laid about 60cm apart and leveled so that their top surface may be exactly the level of the sewer invert, less the thickness of the pipes. The correctness of level of the pipes is to be ascertained by working a straight edge from the invert of each pipe to block ahead.

3.4 The pipe must also be checked at intervals for the proper line and level and the first pipe of any length must be very carefully bedded and leveled into position.

  - The object to be obtained by the method above described is to ensure that the outside of the sockets shall be raised approximately 25mm above the concrete bed in order to allow the joints to be made properly in the under side.

  - In his prices for laying concrete, the Contractor must allow for doing the work in the manner as above described including cost of blocks.

- Junctions on stoneware pipes

  - Where shown on the drawings or where directed by the Engineer Junctions pipes shall be provided at intervals during the construction of sewers, the jointing being effected in a similar manner to the pipe of the sewer in which they are placed.

  - These junction arms shall be closed with stoneware or cement disc and the sockets filled with cement mortar. The trench shall not be filled in until the position and orientation of each junction has been measured and recorded by the Engineer.

5.  Laying of stone ware / DWC pipes on rocky strata:

5.1. In trenches where the soil is rocky & slushy or at road crossings, socket and spigot stone ware pipes / DWC pipes are to be laid on GRB bed & the method to be adopted is as follows:

When the earth is taken out to the proper depth and gradient,  bedding of suitable thickness is to be laid as directed by the Engineer.  The top of this bedding shall also be to the required gradient and to the required hydraulic level.

In case concrete bedding is necessary in shallow trenches of rocky, slushy or road crossings M15 concrete at the bottom and alround the pipe shall be carried out, keeping the hydraulic level as per the approved drawings.

5.2. Junctions on DWC pipes:

Where shown on the drawings or where directed by the engineer junction pipes shall be provided at intervals during the construction of sewers, the jointing being effected in a similar manner to the pipes of the sewer in which they are placed.  These junction arms shall be closed with stoneware or cement discs and the sockets filled with cement mortar.  The trench shall not be filled in until the position and orientation of each junction has been measured and recorded by the engineer.

5.3. Laying & jointing of DWC pipes:

The laying & jointing of DWC pipes shall be done as per IS 4127-1983.  The laying of DWC pipes between the machine-holes is similar to the procedure adopted for laying of stoneware pipes, perfectly true both in alignment and gradient on specified bedding. The pipe shall be laid according to the invert levels provided for the sewer line.  Any variation in levels during execution or any other revision in design, if found necessary shall be carried out by bidder without any extra cost.

After jointing, extraneous materials, if any, shall be removed from the inside of the pipe and the newly made joints shall be thoroughly cured.  Ellastometric rubber O ring are used for jointing the pipes.

5.4. Cleaning of pipes:

As soon as stretch of RCC pipes has been laid complete from machine-hole to machine-hole or for a stretch as directed by owner/engineer, contractor shall run through the pipes both backwards and forwards a double disc or solid or closed cylinder 75mm less in diameter than the internal diameter of pipes.  The open end of an incomplete stretch of pipe line shall be securely closed as may be directed by owner/engineer to prevent entry of mud or silt etc.

If as a result of the removal of any obstructions owner/engineer consider that damages may have been caused to the pipe lines, he shall be entitled to order the stretch to be tested immediately.  Should such test prove unsatisfactory, contractor shall amend the work and carry out such further tests as are required by owner/engineer.

It shall also be ascertained by contractor that each stretch from machine-hole to machine-hole or the stretch as directed by engineer is absolutely clear and without any obstruction by means of visual examination of the interior of the pipe line suitably enlightened by projected sunlight or otherwise.

5.5.  Cleaning out sewers and machine-holes:

During the whole of the work the contractor shall keep interior surface of sewers and machine-holes free from cement mortar, bricks, soil or other superfluous matter and shall handover the sewers perfectly clean and free from deposit on completion.

  - Rubber Ring Joints:

The CI pipes shall be of spigot & socket type with rubber ring joints.  In the case of rubber ring joints the groove and the socket shall be thoroughly cleaned before inserting the rubber gasket.  While inserting the gasket it shall be made sure that it faces the proper direction and that, it is correctly seated in the groove.  After cleaning dirt or foreign materials from the plain end, lubricant shall be applied in accordance with the pipe manufacturers recommendations.

The contractor shall make sure that the plain end is bevelled as square or sharp edged may damage or dislodge the gasket and cause a leak.  When the pipe is cut at site, the plain end shall be bevelled with a heavy file or grinder to remove all sharp edges.

The CI pipes with the rubber ring accurately positioned on the spigot shall be pushed well home in to the socket of the previously laid pipe by means of uniformly applied pressure with the aid of a jack or similar appliance.  The plain end of the pipe shall be pushed into the socket of the pipe, and while pushing, the pipe shall be kept straight.  If any deflections are to be made in the alignment, it may be made after the joint is assembled.  A timber header shall be used between the pipe and crow bar or jack to avoid damage to the pipe while the plain end of the pipe is pushed into the socket either with a crow bar or jack, or lever pullar.  CI S/S Pipes and Specials with rubber gasket (tyton joint) and CI D/F pipes and specials with rubber insertion to the required specification with MS bolt and nuts.

  - Rider sewer:

Rider sewers of 200mm dia SW pipes are provided on both sides of the road where the road width is more than 30m and house service connections are connected to the rider sewer.  The rider sewers are connected to the main sewers at intervals wherever required as per site condition or as directed by the Engineer.  Machine-holes are also provided in rider sewers at 30m intervals.  The procedure for laying & jointing of rider sewers are as per for stoneware pipes for sewer lines.

  - TESTING OF STONEWARE & RCC PIPES, DWC & CI PIPES:

All sewers shall be tested before the filling in of the trench or other excavations.  Testing shall also be done after refilling of the trench or other excavations, if considered necessary by the engineer.  The testing or re-testing shall be carried out by and at the expense of the contractors who shall also provide the necessary appliances and water for the same.  The tests will only be made from machine-hole to machine-hole after the machine-holes connected with the length under test have been completely finished.

The test shall be carried out in the following manner.  The pipes shall be carefully cleared of all earth or materials that may be lying thereon or therein and all joints shall be exposed right round so that through examination may be made whilst the pipes are under test.

The ends of the pipe shall be closed by means of expanding stoppers and all junctions with stoneware stoppers or cement disc fixed in cement mortar.

The last but one pipe at the higher end of the length shall be a junction pipe with the junction arm at the top which will permit of the filling of the length with water and also allow the escape of all air in the pipes.

The expanding stoppers at each end of the length under test shall have a hold in the centre with a small piece of a pipe screwed therein and threaded on the projecting piece to permit of a flexible tube not less than 2m long fixed thereto by a coupling.  At the end of the flexible tubing, the following shall be fixed.

- at lower end of length, a clock.

- at top end of length, a funnel of 15cm diameter.

The top of the funnel shall be fixed rigidly at a height of 30cm above the ground level, or such other height as may be decided by the engineer.

After the above mentioned expanding stoppers have been fixed together with flexible tubing and funnel, the length shall then be filled with water through the junction arm of the pipe provided therefore.  As soon as the water has risen to the level of the filling junction arm an expanding stopper shall be fixed thereon.  After a short time has been allowed for absorption, water shall be poured into the funnel until the same is filled to the top.

If any of joints are leaking & if during a period of ten minutes the water level in the funnel drops 25mm or more (no more water being added or sewer interfered with in anyway during the period) the test shall be considered unsatisfactory.  If the water does not drop more than 25mm and there is no sign of leakage at any of the joints, the test shall be continued for one hour and at the end of the hour the pipe lines including the joints shall be examined and if no indication of sweating or leakage is found then the test will be considered  satisfactory.   Should the test be unsatisfactory, all such joints or pipes found to be defective shall be removed, replaced or re-laid to the satisfaction of the engineer by the contractor at his cost.

The test shall be done as many time as may be necessary until the length is found to be watertight to the satisfaction of the engineer.

The water required for testing shall be clean.  In case of testing of cement concrete sewer pipes of more than 600mm diameter, the permissible quantity of water replenished can be increased by 10% for each additional 100mm dia of pipe.

- Laying of Cast Iron Pipes

  - The laying and jointing of cast iron pipes shall be carried out as follows:

Before laying the pipes, the contractor shall carefully brush them to remove any soil, stones or other materials  which may be therein.  An even and regular bed having been prepared and joint pit excavated to form a recess under the socket of each pipe of no greater   depth and width than to enable the pipe jointing  to be property done.  Each pipe shall then be carefully lowered and placed singly in the trench and shall rest in the solid ground for a distance of not less than two thirds of its entire length.  In places where the soil is not hard, cement concrete bed blocks or timber piles have to be provided under the pipes if directed by the Engineer.

  - Pipes not Truly Laid

Any pipe or pipes laid, which on inspection are found to diverge from the true lines and levels shall be removed and re laid to the true lines and levels and the old jointing properly cleared off the pipes and fresh joints made by the contractor at his expense.  Any pipes damaged in removal shall be replaced by the contractor at his  cost.

  - Cutting of C.I. Pipes

Where necessary and as ordered by the Engineer, the Contractor shall cut the pipes and fix and joint common collars for jointing spigot ends.  The cut ends of the pipe shall be made truly at right angles with the axis of the pipe.

  - Covering up Open Ends

The Contractor shall take particular care to ensure that the apertures and open ends of pipes are carefully covered whenever the workmen are not actually employed therein.

  - Jointing of C.I. Pipes

The trench must be kept quite dry during jointing unless in any particular case the 
Engineer permits laying of the pipe in wet conditions.  Plain spigot and socket pipes shall be joined as follows.

- Flanged Joints

Flanged joint should be made by painting the facing of the flange with white lead freely and bolting up evenly on all sides.

When packing must be used, it should be of rubber insertion of approved thickness.  The packing should be of the full diameter of the flange with proper pipe hole and bolt holes cut out evenly on both the inner and outer edges.  Where the flange is not fully faced, the packing may be of the diameter of the packing strip only.  Proper placing of the packing should be checked before another pipe is joined on.

- Cement Joints

The cement for the joints shall conform to IS 12330/ 1988 specification for Sulphate Resistant cement.

Cement and water taken in proportion 8:1 by weight shall be thoroughly mixed.  The mixture shall be such that when it is tightly compressed by hand into a ball and the ball is broken into two pieces the break shall be clean.  If the hand becomes water stained, it has to be considered that the water is excessive.  If there is evidence of crumbling in the break, water added is less than required.  The cement mixture shall ring with metallic sound while caulked.

Cement  which has been wet for more than one hour or which has undergone initial set shall not be used for jointing.

##### Making the joints

When new pipes are laid close ahead of a newly made cement joint, the disturbance caused during the forcing home of the pipe ends into the sockets during the adjustment of the pipe to proper alignment may damage the new joint.  To avoid this damage, jointing shall be done only when there are atleast six pipes laid to the final grade and alignment ahead of the joint to be made.  Starting at the bottom of the joint space shall be filled with wetted cement and caulked.  The remaining joint space shall than be refilled with cement and caulked until the joint is practically flush with the face of the socket.  The mixture shall be thoroughly compacted to make a water tight joint.

No water shall be allowed to touch the joint until the initial set had taken place.  Immediately after initial set has taken place, the joint shall be covered with wet burlap, or other approved wet materials to ensure complete hydration of the cement.  No water shall be allowed into the pipe until the elapse of 12 hours after the last joint in the line is made.  Filling the pipe with water without pressure after this interval will be beneficial to curing of the joint.

- Rubber Ring Joints

In the case of rubber ring joints or push on joints, the groove and the socket shall be thoroughly cleaned before inserting the rubber gasket.  While inserting the gasket it shall be made sure that it faces the proper direction and that it is correctly seated in the groove.  After cleaning dirt or foreign materials from the plain end, lubricant shall be applied in accordance with the pipe manufacturer’s recommendations.

The Contractor shall make sure that the plain end is beveled as square as sharp edges may damage or dislodge the gasket and cause a leak.  When the pipe is cut at site, the plain end shall be beveled with a heavy file or grinder to remove all sharp edges.

The plain end of the pipe shall be pushed into the socket of the pipe and while pushing, the pipe shall be kept straight.  If any deflections are to be made in the alignment, it may be made after the joint is assembled.  A timber header shall be used between the pipe and crow bar or jack to avoid damage to the pipe while the plain end of the pipe is pushed into the socket either with a crow bar or jack, or lever puller.

  - Fixing Sluice Valve

The sluice valves to be fixed on the pipelines shall be examined, cleaned and placed in the positions as shown in the drawings.  The valves shall be placed on the pipeline and valve chambers constructed according to drawings.  The depth at which the valve is to be laid and the dimensions of concrete and masonry shall be varied when necessary under the orders of the Engineer.

As the pipes in some instances may be required to be fixed at a less depth than will permit the top of the valve spindle being below the level of the road (but this may only be incases where the position of the valve is to one side of the metalloid road) the walls of the valve chamber shall in such cases  be carried upto such height at may be ordered, and the chamber shall have such covering as the Engineer may direct.

The valve shall be supported in the valve chamber so that no stress or strain occurs in the flange or other joints of the valve.

The valve shall be carefully protected from slime or dust by a suitable mat or gunny covering and the pit itself shall be cleared of all unwanted material. All wall chambers shall have provision for diversion of spill over sewage to nearest machine-holes (or) sewer system as per Standard Specification.

  - Fixing Scour Valve

Scour valves shall be fixed at places shown in the drawings or as directed by the Engineer, and the scour connections from the main shall be carried out completely as per drawings.

  - Fixing Air Valve

Air valves shall be fixed at the summits of pipe lines or at places as may be directed by the Engineer.  The air valve connections etc., shall be carried out as per drawing.

  - Interconnection Work

The Interconnection Work between the existing main and proposed main to be laid under this contract shall proceed from the new main to the existing main.  Before actually proceeding with the interconnection work, the Contractor shall make ready necessary tools and plants required for the work at site, such as pumpsets, shoring materials etc., He shall also keep ready at site necessary pipes, specials, valves if any required for the work.  The Contractor shall keep necessary skilled workmen of sufficient strength at site and once the work is commenced, the entire interconnection works shall proceed without interruption by engaging labour for carrying out the work on a continuos basis both day and night till the work is completed.  The work shall be executed as per programme drawn up by the Engineer and shall be completed within the time ordered by the Engineer, for each individual linterconnection.  The work shall be carried out under the direction of the Engineer from the beginning to end.

Laying of Specials, valves (except straight pipes from the branch of the new main to the connecting point in the existing main) including conveying specials etc., from the stores or site of stacking, excavation, timbering, pumping out water from the trenches, lowering, aligning, jointing specials and valves cutting the existing mains, baling out water, inserting the necessary branches, jointing, testing, refilling etc ., shall comprise as one unit of work and will be paid at the lumpsum rate quoted in the schedule for interconnections.

  - Works to be left Water tight

The Contractor shall construct the pipes chambers and all other Works so that they shall be water tight.  Should any leakage appear, it shall be made good by him at his expense by removing and reconstructing the portions of the Work so affected or by other method which will render the Work thoroughly water tight to the satisfaction of the Engineer.

6.12.  Cleaning of Mains

During the execution of the work the contractor shall keep the interior surface of the mains free from cement, brick, soil or other superfluous matter and shall hand over the mains perfectly clean and free from deposit on completion.

6.13.  Masonry Chambers

Chambers for sluice valves, inspection, scour valves, air valves shall be constructed on the pipes in the positions as shown in the drawings or in such positions as the Engineer may direct.  The work shall be done strictly in accordance with the detailed drawings or as ordered by the Engineer.  The excavation shall not be made lower than necessary to admit of the earth being properly timbered.  The bottom of the excavation shall be properly levelled , rammed and a bed of concrete laid thereon.  When the concrete has sufficiently set the building of the brick walls shall then be proceeded with and all iron work fixed in as the building proceeds.  The inside of all chambers shall be plastered with cement mortar 20 mm thick and the outside with cement mortar 12mm thick.  The chamber shall be topped with pre-cast R.C.C. Slab 1:2:4 or cast  iron surface box of  valve cover as ordered by the Engineer.  The surface box or valve cover shall be fixed on the top of the R.C.C. slab by a layer of; cement mortar and sides of the surface box or valve cover covered over with cement concrete.

Where pipes pass through walls of chambers relieving arches shall be turned neatly over the upper half of the pipes or R.C.C. lintels shall be provided to avoid load of the walls transmitted to the pipes.

Cast Iron steps shall be built in each chamber as the Work proceeds on being inserted to every 4 courses of brick work, horizontal distance center to center of each row being 30 cms.

The Contractor shall include in his rate for brick work cost for fixing steps, frame, cover etc., for completing all chambers in accordance with the drawings and with the above specifications.

6.14.  Testing of Main-Hydrostatic Test

After laying and jointing the pipes and specials, the pipe lines shall be tested for hydrostatic pressure in such length as may be specified by the Engineer.

All  pipes, fittings, and valves subject to water pressure  shall be hydraulically tested to the pressure specified  in accordance with the applicable standard as per BIS requirements of pipes/specials.

Unless otherwise specified hydraulic tests to 1.5 times the maximum working pressure shall also be applied at site to all pipework installed by the contractor.

In the case of cement joints, the joints may be tested to a minimum test pressure 3.5 kg/sq.cm.

If cement joints show seepage or slight leakage, such joints shall be cut out and replaced as directed by the Engineer and the test repeated.

The contractor shall make  his own arrangements to procure, necessary equipments, apparatus etc., required for testing and shall provide necessary labour for filling with water the length of pipes to be tested, fixing all apparatus and for carrying on the testing operations until the length of pipes specials and connections are finally passed by the Engineer.

The  length to be tested shall be provided with two blank flanges fastened on in the usual manner by collar bands and bolts to the end pipes or if the length to be tested shall have a sluice value at each end, such blank flanges may be dispensed with.

The length of pipes to be tested shall first be filled in with water from a higher section of pipes already laid or with clean water shall be arranged at the contractor’s expense with the approval of the Engineer.

Before the actual testing pressure is applied any air which has lodged in the length of pipes to be tested shall be got rid of, by screwing on at the highest part of the length of pipes or temporary air valve, or, by opening  a temporary stop-cock or by other mean as the Engineer may direct.

The test pressure shall then be applied to the length of pipes under test by a hand or powered hydraulic test pump.  The connection of the test pump to the length of pipes shall either be at the union connection provided at a blank flange or shall be at a temporary stop cock or fountain connections as the Engineer may in the circumstances direct.

The  actual test shall be made by pumping water into the length of pipes under test, until the test pressure as specified above has been reached on the pressure gauge.

The test pressure shall be maintained for one hour or for such other period of time as may set by the Engineer and each joint will be inspected.  While the pressure is on, the pipes should be struck smartly with a 2 kg hammer.

When a flange joint is found to be leaking, care shall be taken that while tightening up the flanges, the neighboring joints are not affected.

If the length of pipe line under test is found to be satisfactory and no leaks or sweatiness are found at the pipe joints or at the joints of specials and connections then this length of pipe line will be passed by the Engineer.

But should any pipe, joint, special or connection be found to sweat or leak, the contractor shall make good at his cost such defective joint and the length of pipe line shall be re tested by the Engineer until all pipes, joints, specials and connection are found to be satisfactory.

If any pipe or special leaks or bursts, the damaged portion shall be removed and new pipes or specials shall be laid and jointed at the contractor’s  cost.

6.15.  Restoring Road Surface

The surface of the road or ground portion which is excavated for the laying work shall be finished off to the proper level with the gravel filling and plain cemenet concrete with the standard specification except in the case of National and State Highway roads, where the concern departments will do the road restoration for which the restoration amount will be paid by the implementing agency. Should any settlement occur after refilling is completed, and upto 365 days after completion of construction period, it shall be made good at once and the surface restored to the satisfaction of the authority under whose jurisdiction such road or ground may be, all at the cost of the contractor.

6.17. Collection of Rubbish

The Contractor shall, at his cost on the completion of the Work remove all water and all materials or rubbish of every description which may have been collected in the works find a deposit thereof and anything which my have collected within the works during the period of maintenance shall also be removed before the Works are finally accepted  by the Employer.

7.  Laying and Jointing of UPVC Pipes

7.1 The UPVC pipes shall strictly conform to IS 12818:2003 and as amended from time to time and shall carry  ISI marking in every pipe.

7.2 The contractor should procure the UPVC  pipes from a reputed manufacturer.

7.3 The contractor should  furnish the test certificate issued by the manufacturer.

7.4  The manufacturer`s test certificate and third party inspection certificate should be produced by the contractor for the pipes used in the works.

7.5   In addition to third party inspection , wherever felt necessary, the Engineer shall have the power to  test the UPVC pipes for its quality such as specific gravity, impact strength at O”C, internal hydraulic pressure test, diameter, thickness etc, in TWAD Board laboratory.

7.6 The UPVC pipes joints shall be with solvent cement of good quality, conforming to IS IS 12818:2003

7.7  The Engineer, shall  verify, in addition to the test certificate, whether the pipes  are as per BIS, by visual examination, diameter, weight, wall thickness, flexibility, colour etc.,

7.8  All the UPVC specials required for use in conjunction with UPVC pipes,   should be got approved by the  Engineer.

VI. LIQUID RETAINING STRUCTURES

1 General

- The Wet Well shall be executed as per the drawings and specifications and as directed   by  the Engineer.

- The wet well shall be provided with suitable size C.I.D/F. Pipes for inlet and delivery connections and painted with two coats of anti-corrosive paint as per BOQ / Drawing.

Details of all procedures and compliance documents with necessary confirmatory survey, leveling, investigation conducting SBC Test shall be submitted to the Engineer with working drawing for the view of submittals and to obtain Engineer’s approval before each design and execution stage is commenced.

                - All structures in contact with sewage shall be  with   M30  grade concrete minimum cover shall be 25mm.

All structures coming in contact with sewage shall be constructed with Sulphate Resistant Cement.

River sand of good quality as per BIS standards only should be used for all Concrete works for all components of STP

3.	Testing for Water Tightness:

3.1	In case of wet well including machine-holes with top covered, the tanks shall be deemed to be  water tight  if the total drop in water level over a period of seven days does not exceed 40mm.

3.2	If the structure does not satisfy the condition of the test period, the test may be 	extended for a further period of seven days and if the specified conditions of the test are satisfied the structures shall be considered to be water tight.

3.3	In case of unsatisfactory test results, the contractor shall ascertain the cause, make all necessary repairs and repeat the procedure in the preceding clauses until the test has been passed satisfactorily at no extra cost to the Employer.

3.4	Odour Control device will be mandatory and  provided for all liftstations and Pumping Stations.Here Active/Passive Activated Carbon type odour control device is used.

VII. TESTING, ERECTION, TRIAL RUN, COMMISSIONING AND ACCEPTANCE

1	General

This part deals with specifications for - Erection, testing,  trial run, commissioning and acceptance.

1.1	Test Instruments

The contractor shall satisfy the Engineer as to the accuracy of all the instruments used for tests and if required shall produce recent calibration tests, otherwise have them calibrated at his own expense by an independent authority.

2	Test Certificate

Copies of certificates of all works hydraulic tests shall be provided as details.

The contractor shall obtain and submit to the Engineer and to other parties as may by directed, certificates of test of all times, certifying that they have been satisfactorily tested and giving full particulars of such tests.

3	Hydraulic Test

All  pipes, fittings, and valves subject to water pressure  shall be hydraulically tested to the pressure specified  in accordance with the applicable standard as per BIS requirements of pipes/specials.

Unless otherwise specified hydraulic tests to 1.5 times the maximum working pressure shall also be applied at site to all pipework installed by the contractor.

In the case of cement joints, the joints may be tested to a minimum test pressure 3.5 kg/sq.cm.

4	Manufacturer's works inspection tests and guarantees

All schedules of particulars shall be completed and the guaranteed particulars and the efficiencies of the equipment offered at the duties specified will be binding and may not be varied except with the consent in writing of the Engineer.

The Engineer shall be provided with the facility for inspection of all equipment and material and shall be given at least 30 days notice when such equipment or material is ready for inspection of works test.

In addition all other items of equipment not subject to witness testing shall be temporarily erected at the manufacturer's works and tested for satisfactory operation and shall be offered for inspection. Copies of manufacturer's test readings shall be submitted to the Engineer, all prior to packing for shipment .such inspection, examination, or testing, shall not release the contractor, manufacturers or supplier of any item from any obligation under the contract.

Certified copies of manufacturer's test readings of all items shall be submitted to the engineer within 7 days of the satisfactory completion of the test.

Whilst the engineer shall be provided with facilities for witness testing and/or inspection of all items of equipment at the manufacturer's works. He may at his discretion advise that the test shall proceed in his absence. These test shall be made as if in his presence, and duly certified copies of test readings shall be submitted.

Where items of equipment are of identical sizes and duty it may be required, at the Engineer's discretion, that a reduced number of the items be subjected to witness test; however this shall not relieve the manufacturer from the requirement of carrying out the performance tests on all items prior to offering a witness testing.

If after inspecting, examining or testing any material or equipment, the Engineer shall decide that such items or any part thereof is defective, or not in accordance with the specification or performance requirements, he may reject the said items or part thereof, giving to the manufacturer within a reasonable time, notice in writing of such rejection, stating therein the ground upon which the said decision is based. All re-testing shall be at the contractor's expense.

5	Site Testing

The Contractor shall arrange for the full site testing of all items of equipment and shall include Provision of:

a.	All skilled and qualified operating and test staff for the testing of all equipment.

b.	Provision and disposal of all services, lubricants, and fuels other than electricity

c.	All measuring and testing instruments to demonstrate equipment operates to the fulfillment of the works test

d.	All loading weights for the load testing of all lifting equipment

All test shall be carried out by the contractor to the approval of the Engineer.

The Contractor shall be responsible for co-ordinating the programme of site testing of all items and to ensure that all parties concerned are present during any tests to obligate their responsibilities.

Manufacturer's Works Tests

6	Cranes

All cranes lings and lifting beams shall be tested at the manufacturer's works with a load 25% in excess of the rated load. Tests shall include measurement of deflection and speed of lifting etc.

The test shall be repeated at site when erection is complete using test weights to be provided under the contract.

Certificates shall be provided for both tests.

7	Valves

All valve bodies shall be hydraulically tested closed ended to 1.5 times the rated pressure. Isolating value sate shall be tested to the maximum working pressure, at which pressure they shall  be drop tight.

Testing pipelines

General

Pipelines shall be tested in lengths between machine-holes or valve pits or such shorter lengths as the Engineer may direct or permit.

Pipelines shall be tested in the presence of the Engineer.

Fittings required for temporarily closing openings in pipelines to be tested shall be properly designed for this purpose and shall be adequately strutted to withstand the test pressure specified.

The arrangements for testing a pipeline shall include provision for the surging of air from the   peline prior to a water test.

The contractor shall keep a record of all tests in a book which shall be available for inspection and handed over to the Engineer on demand.

Testing pressure pipelines

Each pressure pipeline shall be tested after completion with the exception of any backfilling not necessary for the stability and safety of the work.

Prior to the testing of a pressure pipeline valves shall be checked and sealed. The pipeline shall then be filled with water and the air released. After having been filled the pipeline shall be left under operating pressure for at least 24 hours so as to achieve conditions as stable as possible for testing.

The pressure in the pipeline shall them be raised steadily until the test pressure of 50% excess  of the maximum working pressure is reached in the lower part of the pipeline and the pressure shall be maintained at this level by pumping if necessary for a period of one hour. The pump shall them be disconnected and no further water shall be allowed to enter the poplin for a period of one hour. At the end of this period the original test pressure shall be restored by pumping and the loss measured by drawing off water from the pipeline  unit the pressure as at the end of the one hour test period is again reached.

The permissible loss for pressure pipelines under test shall not exceed 20 liters per mere nominal bore per kilometer length per bar of pressure (Calculated as the average pressure applied to the pipeline) per 24 hours.

Gauges used for testing pressure pipelines shall have a dial diameter of not less than 150 mm and a full-scale reading not greater than twice he specified test pressure. before any gage is used the contractor shall arrange for it to be checked independently and data certificate of its accuracy shall be provided for the Engineer.

The contractor shall make his own arrangements for the supply and disposal of water used for testing which shall be obtained from a source approved by the engineer.

Test on Instruments

The contractor shall carry out on-site pre calibration test to demonstrate the accuracy of all level, pressure at rate of flow instruments, the transducers, buffers, displays amplifiers, recorders, integrator and transmitters incorporated in the works over a range of flow from the minimum to the maximum anticipated design range in the plant as required by the specification and that the accuracy obtained at the manufacturer's works tests can be obtained on site. The contractor shall supply sets of calibration curves of weirs, flow meters, metering pumps and the like.

Other tests

The contractor shall carry out all other tests required either by himself and or the engineer to prove the plant, and to comply with the requirements specified.

These tests shall embrace all instrumentation, alarms, control systems and processes, all pumps, chemical metering devices, feeders, robes, gages and other components of the plant over the full range of operating conditions.

If, in the opinion of the Engineer, any item of plant is irreparable or insufficient for its purpose or function the contractor shall, without delay, replace the item with another satisfactory item or better unit all at this own cost, paying if necessary, air freight charges to expedite prompt delivery.

Sluice Gate

i.	The contractor shall perform leakage test after installation of the sluice gates.

ii.	Under the design, seating head and unseating head the leakage shall not exceed the limit specified an AWWA 0501/IS; 13319, class I for shop testing.

Instrumentation and control system

Performance of the instrumentation system and function of logic control system shall be checked as per the design requirements.

Recommissioning Trials, Tests

a.	Start up:

On completion of erection of the equipment and before start-up, each item of the equipment shall be thoroughly cleaned and them inspected jointly by the Engineer and the contractor for correctness, completeness of installation and acceptability for start up, leading to initial pre-commissioning test at site. The Engineer and contractor shall as mutually agree the list of pre commissioning tests to be performed.

b.	Trial Operation

The contractor shall prepare a Trial operation report comprising of observations and recordings of various parameters to be measured in respect of the above trial operation. This report, besides recording the details of the various observations during trial run shall also include dates of start and finish of the trial operation and shall be signed by the representatives of both the parties. The report shall have sheets, recording all the details of interruptions occurred, adjustments made and any minor repairs done during the trial operation. Based on the observations, necessary modifications /repairs to the plant shall be carried out by the contractor to the full satisfaction of the engineer to enable the latter to accord permission to carry our performance and guarantee tests on the plant. However, minor defects, which do not endanger the safe operation of the equipment, shall not be considered as reasons for withholding the aforesaid permission.

Commissioning

- The plant shall then be on trial operation of Ninety days during which period all necessary adjustments shall be made while operating, over the full load-range enabling the plant to be made ready for performance and guarantee tests. The contractor shall provide necessary staff.

The trial Operation shall be considered successful, provided that each item     of   the equipment can operate continuously at the specified characteristics,  for  the  period of Trial Operation.

- During the contractor's commissioning/start-up engineers specifically identified as far as possible, shall be responsible for carrying out all the pre-commissioning tests. On completion of inspection, checking and after the pre-commissioning tests are satisfactorily, over, the complete plant shall be placed on initial operation during which period the complete equipment shall be operated integral with sub-systems and supporting equipments as a complete plant.

iii.	Any special equipment, tools and tackles required for the successful completion of the performance and guarantee the contractor free of cost shall provide Tests.

iv.	The contractor during these performance and guarantee tests shall provide the guaranteed performance figures of the equipment’s. Should the results of these tests show any decrease from the guarantee values, the contractor shall modify the equipments as required to enable them to meet the guarantees. In such case, performance and guarantee tests shall be repeated within one month from the date the equipment is ready for re-test and costs for modifications including labor, materials and the cost of additional testing to prove that the equipment meets the guarantees, shall be borne by the contractor.

Performance and guarantee tests shall make allowance for instrumentation errors as per specification.

Acceptance

- The employer will certify no item of plant for acceptance unless it has successfully passed the entire test called for under the contract. If nevertheless the employer uses only part of the works, that part which is used shall be deemed to have been accepted at the date of such use. An acceptance certificate for plant shall not be issued unless the following documentation are duly compiled and submitted in final formats in duly bound volumes.

i.	A compilation of all shop inspection results/reports of the plant/machinery with due attestation that the plants have been manufactured to specified standards (6 copies).

- All erection/ construction quality control checks in appropriate approved formats for all installation works with attestation that installation has been carried out as per acceptable/stipulated standards (6 copies)

- Operating manuals and Warrant Certificates

On completion of the operation period of 5 years, the plant shall be handed over to the employer for the further operation and maintenance.

VIII. ELECTRICAL WORKS AND PUMPING MACHINERY

## A	ELECTRICAL

1	General

Following clauses specify General Electrical requirements and standard of workmanship for the equipment and installations. General specification classes shall apply where appropriate except where particularly redefined in the Special Specification Clauses.

2	Standards

The equipment offered shall comply with the relevant Indian Standards. The equipment conforming to any other approved International Standards which is considered equivalent or superior shall be acceptable. The bidder however, shall have to substantiate equivalence or superiority.

3	Requirement of Statutory Authorities

The electrical equipment/installations shall comply with the requirements of Rules/Regulation as amended up-to-data, required by Statutory Acts or Authorities.

-	The Indian Electricity Rules, 1956

-	The Indian Electricity Act.

-	The Indian Electricity (Supply) Act, 1948

-	The requirements of Chief Electrical Inspector to the Government of Tamil Nadu.

-	The requirement of Tamil Nadu State Electricity Board.

-	Fire advisory Committee Insurance Act.

-	The contractor shall get the drawings, layouts of HT sub station etc. approved from TNEB and chief Electrical inspector to the Govt. of Tamilnadu, wherever necessary. The contractor also shall arrange to get the installation inspected by CEIG and carryout modifications/ rectification as required by CEIG, prior to commissioning of sub station/electrical equipments.

4	H-Frame Steel Structure

H-frame galvanized steel self supporting structure shall generally have the following equipments.

-	Lightning Arresters

-	Gang Operated A.B Switch

-	DO Fuses

-	String Insulators

-	Pin Insulators

-	ACSR conductors of appropriate sizes to connect all the equipments

4.1	Lightning Arrester

Lightning arresters shall be provided on each 11KV line before the termination on the 11KV isolators in the switch yard. Lightning Arresters shall be suitably mounted on H pole structure or 4 pole structure for receiving 11kv supply  as per IS 3070  Part I.

4.2	Gang Operated AB Switch

The Switches shall be provided with horizontal connecting bar, for gang operation, G.I pipe as down rod lever coupling and operating handle with padlock and other components necessary for complete assembly.

4.3	 11KV Drop-Out Fuses

The IIKV drop-out fit off fuses shall offer protection against short circuit and suitable for use in conjunction with 11KV system having fault level of 500 MVA as per relevant ISS.

A suitable insulated operating rod shall be provided with each fuse assembly. Two pairs of rubber hand gloves for working on 11KV shall be provided.

4.4	Insulators

The disc, pin and post type insulators used shall be of high quality glazed porcelain. The electrical and mechanical characteristics shall conform to IS:731 and IS:254. The insulators shall have following characteristics suitable for use in an effectively earthed system.

-	System voltage				:	11kv

-	Dry Wet one- minute power

Frequency to withstand

voltage					:	22 kv

-	1.2/50 micro second impulse

withstand voltage			:	75KV

-	Power frequency puncture

withstand test voltage on

units					:	1.3 times of the dry flash over voltage of the unit.

-	Visible discharge voltage		:	9 KV

-	Total minimum creep age

distance for post and disc

insulator				:	320 mm for post insulation

320 mm for disc insulation

## 5   LT  Panel Board

## Panel board shall be either cubicle type floor mounted or wall mounted. The board shall be Vermei and dust proof powder coated made of 14 SWG MS sheet and MS 	angle, iron frame work with copper/Aluminum bus bar 4 nos enclosed with insulated sleeves of approved colour  and required current carrying capacity as per IE rules. The 	bus bars shall be mounted on a suitable insulating support. The panel board shall be complete with all internal wiring including twin copper earthing.

6    Air Circuit Breakers

The Air Circuit Breakers shall conform with IEC/Indian standards.  The ACBs shall be manually draw out type in open execution with over current trip device adjustable 64% to 110% time setting for overload adjustable current setting for short circuit protection and adjustable current and time setting for earth fault protection.

No. of poles				- 4 or 3

Rated insulation voltage 		– 1000

Rated short circuit breaking  	- 50 KA – (AC – 415V)

Rated making capacity AC 		– 105KA

Rated short time withstand current – 50KA

Total making time 			– 30 millisecond

Total Breaking time 			– 38 ms.

Motorised mechanism 		– 220/240V

Under voltage released AC 		– 150/(66)VA

Opening line delay 			– 20 – 30 MS

System protection 			– overload, short circuit, Earthfault

Overload protection 		     – adjustable current settings ariation 							50%  to 100%

Short circuit protection 		– adjustable pickup level

Earth fault protection	– 	        relay shall have sensitivity of 								adjustable Between 10% to 30% 							of ACB rating

Air circuit Breaker shall be fitted with following

- Heavy duty switch having not less than 4 No. + 4 N C - contacts

- Built in resin cast current Transformer

- Auxiliary contacts

- Shunt and under voltage tripping device

- Neutral CT for earth fault protection

- ACB shall be suitable for locking the breaker in various positions.  Provision of door locking with requisite end termination lug and sockets.  Terminal bars for connecting more than one terminal.

7	Moulded case circuit breakers

The Moulded case circuit Breakers shall have overload, and Short-circuit protective elements.  The contact system shall be designed to have minimum wear and also energy loss.  Arc extinguishing device shall be provided.  The MCCB shall have ‘ON’ – ‘OFF’ or ‘Trip’ indicators.  The interrupting capacity of the breaker shall be 35KA – 50 KA at 415V.  The MCCB shall be tested as per IS 2516.

The container shall be of non-conducting materials and withstand high temperature, and flame retardant.

8	  Miniature Circuit Breakers

Miniature circuit breaker working on residual current device having 6000A short circuit breaking capacity and 30 milli amp. sensitivity and 30 millisecond tripping time conforming to IS 12640 trip free mechanism operating for rated leakage at nominal 10 Volts.  Earth leakage circuit breaker also may be provided wherever necessary instead of  MCB.

  - Fuse Switch Units.

The fuse switch unit shall be suitable for 415/430V operation and conform to IS 13947 (Part 3) and IEC 947-3.

The switch shall conform to following Technical specification

Rated operational voltage	- 415V

Rated insulation voltage		- 660V

Rated Thermal current		- 125A/160A/250/400A

Number of Poles			- Three (TPN) isolate

Rated operational current		- as required

Rated making capacity		- 10 times the rated current

Rated fuse short circuit making

capacity at 415V			- 176 KA

Rated fuse short circuit withstand

capacity				- 80 KA

  - Indicating Instruments

All electrical indicating instruments shall be digital square type of size suitable to the panel.  These shall be suitable for flush mounting with only flanges projecting on vertical panel.  Instrument dial shall be white with black numerical lettering.

Instrument shall conform to IS 1248 and shall have accuracy class 1.00 or better.  The current coil and potential coil of Ammeters and Voltmeters respectively, shall withstand 120% of rated current and voltage, without loss of accuracy.

The meters shall have external zero adjustments.  The ammeters fitted in the motor circuits shall have suppressed scale to indicate the maximum starting current.  The instrument shall be provided with glass cover to avoid the possibility of measurements due to static charge.

The three phase three wire trivector meter shall comprise of KWH meter and KVAH meter mounted together with KVAH meter in one case with special summator mounted between them to register correct KVAH at all power factors.

All the factors shall have respective maximum demand indicators to record the average power over a period of half an hour.  The trivector meter shall conform to relevant IS.

9.3	Under Voltage Relays

The induction disc type, single pole under voltage relay shall have inverse time voltage characteristics on all taps. The relay shall be designed to develop maximum torque at supply frequency and shall be insensitive to the voltage at harmonic frequencies.

The operating time shall be adjustable by time setting multiplier. Selection of the required voltage setting shall be possible by means of a plug setting bridge having an insulated plug. The relay shall conform to IS-3231.

10	Protective Relays

Relays shall be rectangular in shape, flush mounting type, having dust tight covers, removable from front, and shall be equipped with externally reset, positive action operations indicators. The relay shall have auxiliary units of either series connected or shunt connected type. All auxiliary relays shall be non-draw out type and protection relays shall be draught type with test facilities.

Test plug shall be supplied loose. All relays shall conform to the requirements of IS - 323 or relevant IEC in general and IS - 3231 in specific.

Relays shall be provided with adequate number of potential free self reset/hand reset output contacts as required. Provision shall be made for easy isolation of trip circuits of each relays for the purpose of testing and maintenance. Current transformer short circuiting arrangement shall be provided in case of draught type relays.

Voltage relays shall have sufficient thermal capacity for continuous energisation using external resistance, if necessary.

No control relay, which will trip a circuit breaker when relay is de-energized, shall be used.

11	CABLES

- 11.1		1100V/660V Grade cables shall be PVC insulated, PVC sheathed, G1 strip armoured, Aluminum conductor.

The control cables and cables for lighting system shall be with PVC insulated, multi stranded copper conductors.  Cables in general shall conform to IS 694, IS 1554 part I & II, and cross section 25,16, 10, 6, 4, 2.5 and 1.5 sq.mm.

- 11.2	Laying of cables

- Cables shall be laid directly buried on earth, in conduits along walls, ceiling etc.  The cable installation shall conform relevant ISS.

- Cable inside the Sub-station/Building shall be laid in the prepared trench.  If any hole or breaking of wall is required for cable laying work, it shall be done by the contractor and the wall shall be closed after completion of the work as original.

- The cable trench dimensions inside the Sub-station and the route shall be indicated to the civil contractor well in advance while Sub-station civil work is in progress, depending upon the cable entry, and location of different equipments, transformers, panels, etc.

- Laying of underground cables outside the building shall be done by excavating a trench covered by brick and sand of 0.75 metre depth for HT and LT cable and protecting each run of cable by sand and earth filling.

- The HT and LT cables shall be taken through the cable duct provided on the ground floor roof as shown in the sketch, by properly clamping.

- Fixing of cable on the wall by clamping the cable, using suitable GI clamps with wooden saddles. The distance between two clamps shall not be more than 750mm.  The cables shall also be taken through PVC pipes on the wall.  The cable route on the walls shall be decided with the Engineer in site.  The cables shall be covered with GI plates, trays or wooden covering.  Sharp bending, twisting and Kinking of cables shall be avoided.  Suitable cable duct shall be provided in the wall connecting all switch rooms of Railways and Commercial Complex.

12.	 	Distribution Boards

All the switch Boards, Panels shall be neatly wired using 1100/660V PVC insulated stranded copper cable of minimum 2.5 sq.mm.  Copper Bus Bars also may be provided to suit the requirements.

Each wire shall be identified at both ends with cable marker.

Distribution Boards shall be housed in metal clad case or board conforming IS 4237. The Sub-distribution Boards shall be equipped with rigidly fixed miniature circuit breaker complying IS8828 in the phase leads with over load and short circuit protection.  The MCBs shall have adequately sized terminals for the outgoing leads.  The distribution boards shall have adequately rated phase and neutral bus bars of high conductivity copper.  Earth bus bar with the necessary number of terminals for connecting the earth continuity conductors.

Each SDB shall have circuit schedule pasted or permanently fixed inside the cover stating the details of circuit controller and rating of MCB.  Non-flammable insulating shields shall be provided to prevent fire hazards during operation of MCBs.

The Sub-Distribution Boards shall not be mounted at a height exceeding 180CM from ground level.

Main Distribution Boards shall be surface mounted.  Main Distribution Boards shall be erected in each switching room, and sub-distribution boards shall be located according to the distribution of load and the equipments to be connected and its location.

## 13.	Lighting System

13.1	Point Wiring

Point wiring shall include all work necessary to complete wiring from switch circuit of any length from the tapping point on the distribution circuit switchboard to the following:

- Ceiling rose for fans, lighting etc.

- Socket outlet (in the case of socket outlet points)

- Lamp holder (in the case of wall brackets, batten points, bulk head and similar fittings).

- Call bell buzzer (in the case of the works “via the ceiling rose/socket outlet or bell push where no ceiling rose/socket outlet is provided”).

    - Circuit wiring

Circuit wiring shall mean the length of wiring from the distribution board upto the tapping point of the nearest first points of that circuit, viz., upto the nearest first switchboard measured along the run of wiring.  Such wiring shall be measured on linear basis.

14	Electric Motor

Type      :	Squirrel case induction motor suitable for continuous duty.

Standards    	 :   Performance - IS 325, IEC 34

Dimensions - IS 1231, IEC 71

Site condition		:	 Ref. Ambient -45C

Max humidity - 100%

Cast iron body with integral feet and frame. The stator core shall be that of high grade carlite insulated low loss silicon steel lamination stacked together and fully tightened. The rotor shaft made of high grade forged/rolled steel. A spacious terminal box to be provided to accommodate aluminum conductor cables. Motor load/HP rating over and above break horse power (BHP) of pump shoud be relevant for sewage service Submersible type heavy duty pumpset.

Technical Particulars:	     Rated voltage: 415V+ 10%

Frequency: 50Hz+ 3%

Temperature rise of 75oC over ambient of 45oC

Enclosure: IP 55

Type of cooling: Totally enclosed fan cooled

Acceptable makes		Siemens, NGEF, CGL, KEC

14.1	Auto transformer starter

Automatic auto transformer starter shall be assembled in 14 SWG sheet steel, floor mounted with following accessories

- Oil immersed auto transformer with 50%, 65% and 80% tapping including  first filled oil.

- Bimetallic overload relay

- Timer on delay and off delay.

- Ammeter with CTS and selector switch.

- Voltage with selector switch.

- No voltage release

- Indicating lamp, Power On, Trip

( Single phasing current sensing preventor with protection CTS)

- Thermo stat  for oil temperature.(Optional)

14.2	Diesel Generator

Diesel Generators are the Silent AMF Type in to ensure non-exceedance of mandated NHV levels.

Proper installation of exhaust stack as per norms and obtaining necessary consent/NOC from PCB and CEIG including providing changeover panel.

15		Earthing

-	Earthing in general shall comply with C.P.(Code of Practice) 3043 of Indian Standards.

-	Earth electrode either in the form of pipe electrode or plate electrode should be provided at all premises for providing earthing system.

-	As far as possible, all earth connection shall be visible for inspection and shall be carefully made.

-	Except for equipment provided with double installation all the non-circuit carrying metal parts of electrical installation are to be earthed properly. All metal conduit trunking cases. Sheets, switch gears, distribution fuse boards, lighting fittings and all other parts made of metal shall be connected to an effective earth electrode.

-	The main earth electrode should be a Copper Plate G.I perforated pipe driven into the soil as per standard practice. continuous looped eathing should be provided with adequate size G.I. wire /feat. Earthing work should conform to I.E. Rules.

-	The electrodes shall be situated at a distance not less than 3.0 m from the building fencing structure and equipment foundations. The earth pit shall conform to IS: 3043 and GI earth electrodes of not less than 100 mm external dia shall be driven to a depth of at least 3 ma in the ground below the ground level. The surrounding the electrodes, soil shall be treated up with salt, coke and charcoal.

-	Earth electrodes shall be installed near the main supply point and shall comprise a copper/GI earth of appropriate diameter and driven to depth of 3 metres below ground level,. or to a greater depth, if so required to obtain a sufficiently low earth resistance value. Alternatively copper plate mach be used as the main earth electrode conforming to IS: 3043. The electrodes shall be driven at least 3 m away from the building or any other earth station.

Minimum requirement of earth pits as per I.E. rules are as under:

-	Two numbers independent for transformer body

-	Two numbers independent for transformer neutral

-	Two numbers independent for four pole structure

-	One number for lightning arrestors.

-	Two numbers of L.T. panel at sub-station and at pump house.

the main earth electrodes after being driven into the ground shall be protected at the top by constructing a concrete or block masonry chamber of size 300 mm x 300 mm x height 300 mm. and shall be provided with CI cover. The resistance of any point in the earth continuity system of the installation to the main earth electrode shall not exceed 1.0 ohm. The remaining space in the borehole shall be filled with bentonite. The bentonite will hold the earth rod in position. The neutral conductor shall be insulated throughout and shall not be connected at any point to the consumers earthing system.

-	An earth continuity conductors shall run continuously from the farthest part of installation to the main earth electrode and shall be connected by branch conductor to all metal casing and sheating housing electrical apparatus and/or wires and cables. all branch shall be connected to earthing. The earth continuity conductors shall have a cross-sectional area at least half to the size of the phase conductor and in no case less than 1.5 sq.mm of copper/GS.

-	All earth wires and earth continuity conductor shall be galvanized M.S flats of appropriate size. Interconnections of earth continuity main conductors and branch wires shall be brazed properly, ensuring reliable,. Permanent and good electrical connections. The earth lead run on structures must be securely bolted. Neutral earth leads shall be run on separate supports without touching the body of the transformers. Earth wires shall be protected against mechanical damage and possibility of corrosion particularly at the junction points of earth electrodes and earth wire interconnections. Earth electrodes shall be connected to the earth conductors using proper clamps and bolt links.

-	It shall not be allowed to use the armour of the incoming feeders cable to the sub-distribution board as the only earthing system.

-	Sheathed lugs of ample capacities and size shall be used for all underground conductors for sizes above 3 mm2 whenever they are to be fitted on equipment of flat copper conductor.

-	The lugs shall be fitted on equipment body to be grounded or flat copper only after the portion on which it is to be fixed is scrubbed, cleaned of paint or any oily substance on a subsequently tinned.

- No strands shall be allowed to be cut in case of stranded ground round conductors. G.I embedded conduits shall be made eclectically continues means of good continuity fixing and also be rounding copper wires and approved copper clamps.

15.1	 Earthing of Lighting Poles

All external poles are to be looped together with continuos 8 SWG GI earth wire clamped at dollies provided on every fuse box of poles and looped onwards to the other pole. Every fifth pole shall be connected to earth through an earth electrode.

15.2	 Earthing for Lighting Installation

This shall be common grid system, the main grounding conductor laid and embedded in concrete being grounded at earth pits outside the buildings at approved locations or other places. The earthing of L.T. panels shall be connected to two main grounding conductors each of which along with main cables shall run with cables to distribution boards in which floor. This shall run along with th4 cable and at the top floor be connected same section completing the grid.

15.3	Sizes of Earthing Conductors

SL.       System			   Earthing conductor size and Material

No

Buried in ground/ Above ground concrete

-	Main earthing grid		40 X 10 mm MS    	 ---------

11 kV outdoor sub-station	40 X 10 mm MS	50 X 6 mm GS

and 11 kV switchgear

-	415 V switchgear,		suitable to  its  	Suitable to its rating.

transformer, DG set,

Capacitor Control Panel

- 	Battery charger				-	25 X 3 mm GS

-	415 VLT Motors

-	Valve motors				10	SWG GS wire

- 	0 - 15 HP 				8	SWG GS wire

-	15 - 40 HP 				4 	SWG GS wire

-	40 - 50HP 				25 X3 mm GS flat

-	50 HP and above			25 X6 mm GS flat

-	Lighting distribution Board,		25 X 3 mm GS flat

30 V DC Tripping Unit.

-	Local Push Button stations,		14 SWG GS wire

Junction Boxes.

-	Lighting and receptacle system	12 SWG GS wire

-	earth Electrode	          	50 mm dia. 3000 mm long heavy duty

GI Pipe electrode

-	Street lighting Poles			8 SWG GS wire

Notes:	1.	Conductors above ground shall be galvanized steel to prevent  atmospheric corrosion.

2.	Conductors buried in ground or embedded in concrete shall be mile  steel.

- Drawings; The typical earthing details are shown on drawing.

15.4	Battery, Battery Charger & DC Distribution Board

-	The charger and DC distribution board shall be enclosed on a common sheet steel enclosure with necessary compartment for each incoming and outgoing feeder.

-	Complete information regarding battery layout, space requirement for locating battery, wall painting of battery room floor, ventilation, method of lighting etc. shall be supplied by the Contractor. The battery room shall preferably be located inside MCC room as shown,. The battery room shall have acid proof tiles as flooring and upto 4 ft. level. Also there shall be an exhaust fan of appropriate capacity to extract vapours from the room.

15.5 	Tests

-	Batteries and battery chargers shall be routine tested before despatch,in accordance with Indian Standards. Capacity test shall be carried out on the batteries at site after installation.

- 16.		Street Light

Street Light fixtures shall be complete with integral semi-cut off lantern with glass cover complete with internal wiring, control gear, mounting accessories, street light bracket for HPSV 150W made from 60mm dia (B Class G I Pipe) 2 m in length and welded to the pole cap of size 100mm and 30 cm long duly welded.

- 17.	 Street Light Poles

The street light mast shall be 65m/75 diameter G.I pipe of 7.5 meter long with 300mm x 300mm x 6mm of M.S base plate, duly welded at the bottom. A suitable MS box to have 5A control switch, 16A fuse unit with suitable frame work shall be fitted in the street light mast with door and locking arrangements.

A terminal box with fuse shall be fixed in all the poles.

18.	Capacitor

To improve the power factor capacitor shall be provided in the LT bus bar in the sub station.

- The capacitor shall be as per ISS 2834 and IS 2544.

- The capacitor shall be all polypropylene film capacitors. The film shall be  oriented bi-axially.

- The oil used for impregnation under vacuum shall highly purified non- toxic.

- Low loss discharge resistance, to reduce the residual voltage to 50V or less within one minute after the capacitor is disconnected.

- The capacitor container shall be painted with epoxy-based paint, to prevent corrosion/rusting.

- 4 stage switching ON/OFF shall be provided to match with the load.

- Automatic Power Factor Correction Unit shall be provided if necessary.

19.	Safety

The following minimum safety equipments shall be supplied and installed in the   Sub-Station switch rooms and Diesel Generating rooms.

- Portable chemical fire extinguishers conforming to IS 935 or its latest version shall be supplied and installed at the Sub-Station, Switch rooms and Diesel Generating Stations.

- Fire buckets with M.S. angle stand each consisting of 4 Nos. round bottom fire buckets painted with red and marked fire and filled with clear dry river sand shall be supplied and installed at a convenient locations at the proposed Sub-Station.

- First-Aid boxes equipped fully with required materials, shall be supplied and kept at a convenient place in the Switchgear room so that the same is easily accessible.

- Shock Treatment chart.

- Rubber matting of not less than 25 mm. thick and 600 mm width and standard lengths, shall be provided in from of all the switch gear panel, Transformer, Control cubicles, etc.

- Rubber gloves tested for 15 KV about 4 sets shall be supplied.

20	Statutory Approval

The Contractor shall be totally responsible for obtaining statutory approval from the electrical inspector or any other statutory authority for the entire installation carried out by him unless otherwise specified and agreed. Necessary test reports shall be submitted by him to electrical inspector. This will be an integral part of the contract and shall not be paid for separately.

21	Acceptance of Installation

On completion of the work the Engineer, together with the Contractor, will carry out an inspecting of the installing. The Engineer will issue a completed copy of the Purchaser's Acceptance of Electrical Installation to the Contractor as confirmation that the work has been accepted, subject to any matters noted on the form being attended to.

IX.  PUMP SETS AND ACCESSORIES

# 1	General

1.1	  All the Materials used shall confirm to the relevant BIS and should be delivered at site of work.  The Contractor is responsible for safe custody of machinery and other equipments under this contract till handing over to the employer.

1.2	The rates should include all the minor items of civil works, if any required for installation complete.

1.3	All necessary civil works for erection of all equipments and accessories offered by the contractor under this contract should be done by the contractor

1.4	Test certificates for machinery and equipments should produced along with supply

1.5	The bidder should enclose the performance curve duly indicating the duty point for the size of the impeller selected (family curve should not be furnished).  The Performance curve should furnish complete range of operation and the curve should be authenticated by the manufacturer or his authorized dealer.  In the event of non compliance the offer shall be summarily rejected.

  - The contractor shall make necessary arrangements to get supply of electricity from TNEB for operating the machinery and equipment.  Necessary payment to be made to the EB shall be borne by  the employer

  - Before supply of machinery, equipments and other accessories prior approval of the Engineer should be obtained giving the name of makes and other details required.

1.8	Obtaining approval of electrical layout diagram for the installation of all the equipments (transformers, generators, pumpsets and other accessories) and obtaining safety certificates on completion of work from Chief Electrical Inspector to Government of Tamil Nadu should be arranged and got approved by the contractor at his cost.

1.9	All the materials should be supplied as per BOQ and should be of standard makes mentioned below:-

| Sl No | Description | Make |
| --- | --- | --- |
| 1 | Submersible non clog Pump | Kirloskar/ Kishore/ KSB/ AQUA/ Grundfos |
| 2 | Make of Motor | Jyothi/ NGEF/ GEC/ Crompton/ AQUA & Greeves/ Siemens |
| 3 | Make of Transormer | Kirloskar/ GEC/ Indo TECH/ Hidustan |
| 4 | Diesel Generator | Kirloskar/GEC |
| 5 | Starter | Built by any CPRI approved panel builder |
| 6 | Switch Fuse and circuit breaker | L&T/ Cutler Hammer/ Siemens/ Schnider |
| 7 | Cables | Finolex/ Unista/ Uniflex, |
| 8 | Valves | Venus/ Upadyaya/ CALSONS/ Durga |

or approved equal subject to equipment complying with norms by applicable authority such as BIS/EEE etc.,

1.10	The right of choosing the make among the makes offered by the contractors rest with the employer only

1.11	The submersible pumps centrifugal pumps, turbine pumps, submersible motors, motors for turbine and centrifugal pumpset transformer, generators, Panel Boards, to be supplied by the firm will be inspected by the Inspecting Agency fixed by the Employer at the manufacturers premises and test certificate will be issued.  The contractor should make necessary arrangements for the inspecting staff at his own cost for testing the above pumpsets. Final Field testing  pre-and  post-installation   with test specifications,   schedules with  insulation breakdown   tests,  dry run test, heat run tests  and performance   testing approval of the Engineer should be obtained.

  - If the complete plant or any portion thereof is found to be defective the Engineer shall give the contractor a notice in writing to verify such defects.  If the contractor fails to rectify the defects within the specified period the Engineer will rectify the defects at the contractor’s risk and cost.

2	Submersible Sewage pump

Non clog submersible pump set

2.1 General

The submersible sewage pump shall be mono-block type of non-clog design.  It shall be suitable for pumping raw unscreened sewage containing sludge, long fibers, plastic pieces, cigarette butts, etc.  The pump shall be able to pass through soft solids of minimum 100 mm dia and capable of dealing with sewage / sludge with specific gravity of 1.05.  Pumps shall be of 960 rpm for high duty pump and 960/1450 rpm for low duty pumpsets.

Impellers shall be of single / double vane non-clog design.  Additionally, a special contra-block cutting and tearing system should also be incorporated on the suction side of the pump for disposing off soft material which would otherwise clog the pump.

Maintenance free antifriction, permanently grease filled ball bearing shall be provided and this shall take care of all the axial and radial forces at any point of operation.  The weights of the revolving parts of the pumps including the unbalanced hydraulic thrusts of the impellers shall be carried by thrust bearings provided in each pump assembly.

The pump installation design shall be such as to facilitates automatic installation and removal of the pump without having to enter into the sewage pit.  Profile gasket shall be provided in automatic coupling system so to avoid metal to metal contact between the pump and delivery bend to ensure leak-proof joint.

2.2 Pump Constuction

Pump Casing

Pump casing shall be of CI as per IS 210 Gr FG 200 with 2.0% to 3.0% nickel.  The internal surfaces shall be free of rough spots.  The casing shall have centre line discharge.

The high capacity pumps at New Pumphouse shall work in parallel two at a time to discharge peak flow.  Third pump will be stand by.

Impellers

Impellers shall be of stainless steel (CF8M) construction.  Impeller shall be of single/double vane non clog design.  Additionally, a special contra-block cutting and tearing system should also be incorporated on the suction side of the pump for disposing off soft material which would otherwise clog the pump.

Pump Shaft

The pump shaft shall be of stainless steel (SS-410) as per manufacturer’s standard.  The shaft shall be of one piece construciton.

Pump bearing:

Pump bearings shall be of the antifriction type.  The bearings shall be able to take normal thrust loads due to unbalanced hydraulic loads on the impellers plus the weight of all rotating parts of the pumps.  Pump bearings shall be designed with a minimum life of 40,000 hours.  The bearings shall be grease lubricated for life and shall be maintenance free.

2.3  Mechanical seals:

Double mechanical seal shall be provided to prevent pumped liquid entering into the motor winding.  The seal shall be situated in oil chamber to ensure proper lubrication.

The face combination of lower mechanical seal shall be Silicon carbide Vs Silicon carbide and upper mechanical seal shall be Carbon Vs Chrome steel.

Moisture sensor:

Moisture sensor (seal monitor) shall be provided in the oil chamber to detect the failure of the mechanical seal.

The sensor will drip the pump motor in the event of increase of moisture into the oil chamber.

2.4 Lifting chain:

Each pump shall be provided with carbon steel lifting chain of adequate strength.  The chain shall have rings of same sizes as chain, fixed at an interval of about 1 M for engaging the hook of the chain pulley block.

2.5 Foundation Nuts and Bolts:

D.D. Foundation shall be provided

2.6 Protective coating:

The pump shall be epoxy painted.

2.7 Pump balance:

All rotating parts shall be statically and dynamically balanced as per the relevant standards.

- Electrical specifications:

Submersible motor:

The submersible motor shall be dry squirrel gage type, suitable for three phase supply, continuous duty, with class F insulation.  Winding of the motor shall be impregnated by resin.  Motor shall have integral cable entry port and cable entry shall be properly sealed.

The pump motor may often requires starting after intermittent clogging.  The motor should therefore incorporate aluminium die cast rotors only to ensure better starting torque characteristics.

The enclosure for motor shall be IP 68.  Each phase of the motors shall be provided with thermic switches or bimetallic electromechanical temperature detectors.  The motor shall operate satisfactorily  at all operating levels in wet well.

Motor shall be sealed against entry of liquid being pumped by using two mechanical seals.

- Motor:

Type of motors.

The motor shall bne capable of developing the mechanical output for the required conditions, shall have coantinuous normal rating to suit the maximum load when operated at the pump speed.  The efficiency and power factor shall be to start the wide range of load conditions and shall be designed and manufactured in accordance with relevant IS.

The motor HP shall be such that is should safely take the load when the total head is reduced by the rise of water level in river during the flood conditions in the river.

The HP of motor of offered shall have a margin 10% above the BHP absorbed by the pumpset at duty point and also above the mamimum HP absorbed by the pump offered.

Motor load/HP rating over and above break horse power (BHP) of pump shoud be relevant for sewage service Submersible type heavy duty pumpset.

- Spare parts

Supply of spares and tools shall be made as per the list prescribed in BOQ with index card

D/E spanners					1 set

Ring spanners					1 set

Bearing puller 				1 No

Grease gun 					1 No

Hand gloves tested for electrical operation	1 Pair

Ball peen hammer				1 No

Screw Drivers					1 set

Electrical tester				1 No

Electric megger				1No

### 6.	COMPLETION PLANS

The successful bidder shall be requested to furnish completion plans in triplicate within one month from the date of the first testing of the plants.  The plan should show the entire layout of the plant executed.  Five copies of plan should be supplied to the Employer and one to be framed and suspended in the Head works.  The contractor shall in addition to the above furnish detailed specifications of the equipment provided to the Employer with all technical data.

7.	MAINTENANCE MANUAL

The periodical maintenance schedules for each equipment shall be given with reference to the hours of operation.  Detailed information about the spare parts (part name, identification number etc.) should be given.  The copies of the manuals should be furnished within one month from the date of commissioning.

- The contractor should supply one set of tools for the pumpset maintenance of    the machinery and equipments supplied by them under this contract.

## General

9.1      Cable lengths given are only approximate and payment will be made for the actual lengths of cable laid.

  - The contractor has to make necessary arrangements to get supply of electricity from TNEB for operating the machinery and equipments. The necessary service connection and S-D charges will be paid by the Board.

  - Obtaining approval of electrical layout diagram for the installation of all the equipments (transformers, generators, pumpsets and other accessories) and obtaining safety certificates on completion of work from Chief Electrical Inspector to Government of Tamil Nadu should be arranged and got approved by the contractor at his cost.

9.4	Before supply of the machinery equipments and other materials, prior approval of the Engineer should be obtained giving the name of maker and other details required.

10 	Electrical Wiring and installation of fittings

10.1	The materials used for conforms to the relevant I.S.S wherever applicable. The make and other details of materials to be used should be furnished along with the bidder.

10.2	Continuous earth connection are to be made with 14 SWG T.C. wire.

10.3	The wiring work done shall be neat, true to line, level etc. and in such a way that it gives an impressive and aesthetic appearance to the building.

10.4	The actual location and number of points for lights, fans power plugs etc. may be altered at the time of execution by the Engineer.

10.5	Entire wiring and cabling work should be done as per IE rules.

10.6.	Any damages or breakages, chipping etc. caused by the electrification works to the structures have to be rectified by the contractor at his cost to the satisfaction of the Engineer.

10.7.	The Contractor has to test and every point after completion of wiring to the entire satisfaction of the Engineer by taking temporary supply from the existing service.

10.8.	Wiring to light point (both internal and external) and fan point will be treated as complete only when supply as well as connection upto the ceiling rose is completed.

  - Whenever conduit pipe wiring is done, cover for switch boards containing

switches, plugs, etc. should be of hylam sheet or other specified sheet only.

X. OPERATION AND MAINTENANCE PERIOD:

General

Following the Engineer to accept the Contractor has satisfactorily completed the individual tests, final commissioning tests and trial operation of the Works, the Engineer shall issue a “minor outstanding works and defect list”. This “minor outstanding works and defect list” is to provide the details of the defects to be rectified and works that are still outstanding which the Employer can accept the Contractor to finish those works after the Employer has taken-over the Works . The Contractor shall acknowledge completing these minor outstanding works and rectifies the identified defects within the Defects Notification Period.,The Engineer will issue the Taking-Over Certificate for installation and a letter to the Contractor to permit  Operation and Maintenance Period to commence. The Defects Notification Period  is of  12  months duration, shall commence on the same day.

The Employer and the Engineer will arrange to handover of the whole Works to the Contractor, for them to commence the operation and maintenance of the whole  Works. The duration of Operation and Maintenance Period will be 60 months. A Test on Completion for Operation and Maintenance period has to be satisfactorily completed by the Contractor to demonstrate to the Employer that the whole Works is in good operative condition.

Contractor's obligations during the operation and maintenance period of 60  months

During the operation and maintenance period of 60 months of the Works (Operation and Maintenance Period), which  also includes the Defects Notification Period of 12  months, the Contractor shall be responsible for the following:-

(a) Operation and routine maintenance for the whole of the Works, including the provision of all necessary skilled staff and unskilled workers necessary for full operation and maintenance of the works. The Contractor shall provide required persons per shift. In addition, the day shift shall include a supervisor for the whole of the  pumping station. The additional day shift staff shall be available on a "call out" basis to deal with any problems, which may arise outside the specified day shift period. During this sixty  months period, the Contractor shall provide `hands-on' training to the Employer's operating and maintenance personnel, who will be trained to carry out their future duties under the direction and supervision of the Contractor. The Contractor shall be responsible for the work of the Employer’s personnel during this period;

(b) Rectifying defects in accordance with the requirements entered in the “minor outstanding works and defect list” issued by the Engineer for  the Works, including the provision of all supervision, labour, parts and materials including chemicals, fuel and lubricants excluding electricity power charges.

- To Operate and maintain the collection system, all instruments and mechanical, electrical equipments in accordance with the aim and purpose of collection of sewage to STP. The pump station & equipments covered under the above contract will be totally attended to, by the contractor including any “Troubleshooting” to ensure smooth and trouble free operation.

- The contractor will monitor the performance of the collection syatem; conduct the analysis of the sewage collection and transportation to STP. Contractor shall initiate and take adequate actions to ensure smooth and satisfactory performance / running of the system on a 24 hours / round the clock basis.

- The contractor shall prepare and implement an effective maintenance programme in consultation with the Employer.  It is an absolutely contractor’s responsibility to look after all sorts of maintenance whether preventive, Minor, Major, or break-down

- The contractor should plan & procure all spares, and all consumables including spare pipes jointing materials, Diesel for vehicles, etc. Further the contractor will plan about the requirement well in advance (At least 3 months) and procure the material from the market.

- The contractor will be responsible for keeping up-to-date record of documents including History Card for equipments and maintaining every day log book relating to various analysis performed.

- The contractor shall maintain and update logbook, in which details of operational      parameters are recorded in every shift and at regular interval say hourly or as decided mutually.

- The contractor will prepare and submit a daily report of pump station performance and will assist the Employer in preparing the necessary documents for their purpose and records.

- The contractor will be responsible to carry out day to day periodic maintenance, necessary to ensure to smooth and efficient performance / running of all equipments / instruments comprising the collection system and maintaining the record of the same.

- The contractor shall have to issue identity cards with photographs to all the staff employed for Operation and Maintenance. The list of the same shall be submitted to the Employer mentioning qualification & experience.

- The contractor will employ minimum staff for operation and maintenance of the Collection system as  detailed below. The contractor will employ no offense, guilty person or indiscipline man.

| MINIMUM STAFF REQUIREMENT |  |  |
| --- | --- | --- |
|  | A. Pumping/Lift station |  |
|  | Electrician grade - II | 1 1 No |
|  | Watchman / Helper | 1 No |

| B. Sewer network |  |
| --- | --- |
| Technical Assistant | 2 Nos |
| Sewer Inspector | 6 Nos |
| Sewer Cleaner | 12 Nos |
| HSC Cleaner | 4 Nos |

The work shall be carried out on a 24 hr basis, without intermission and the staff deployed by the

contractor shall be in accordance with this contract.

- The above staff shall be distributed in three shifts as per mutual agreement between Contractor and Employer  As per agreement the number of staff in each shift should always remain present otherwise penalty towards absence of any staff shall be  recovered from the Contractor. The contractor shall make the arrangement of reliever for weekly off/holiday etc. Absence on any ground like weekly off or holiday shall not be considered. The presence of staff in each shift should be marked in muster to be maintained at office of shift in charge shall be considered as final. The Contractor’s staff must mark their presence in this muster.

The Contractor may maintain a separate register for his own purpose.

The staff of contractor will always remain in contact with the Junior Engineer, Assistance Engineer deployed by the Employer and follow their instruction.

Unsatisfactory and inefficient running of the system and unnecessary and excessive usage of spare, consumable, etc. supported by the reasons which are under control of contractor will be highly objected. In such cases Engineer’s decision will be final and binding to the contractor.

Contractor will comply with all safety rules and regulations and all inter disciplinary as followed by the Employer.

The Employer will not be responsible for any accident /injury to the staff of the contractor. Further the Employer will not provide any insurance or medical facility to the staff of contractor. The responsibility lies with the contractor.

- All Central/State Government / Semi-Government / Local Body’s Rules and Regulations pertaining to this contract shall be followed and observed by the contractor without any extra cost to the Employer.

- The duration of the O&M shall be 60 months from the date of successful commissioning of the collection system. The contractor should employ all the staff within two days of successful commissioning.

- The contractor will provide the necessary tools and tackles required for day-to-day maintenance.

- The scope of work also includes cleaning of complete pump station area including floor, toilet block railing, door, windows, light fixtures and ceiling etc. The entire premises of the pump station area shall also be cleaned and maintain by the contractor regularly.

- This work is inclusive of but not limited to operation, maintenance, house keeping, cleaning, removing sludge by its own carrier arrangement & dispose it off as per Employer’s  instructions. Preparing data recording, correspondence work to EMPLOYER and Government Departments, etc. All this work should be done as per standard practices and by following labour, factory, electrical, TNPCB, and all other old and new law and order, Indian standards etc. as applied of Local, State and Central Government of India.

- Right is reserved by EMPLOYER of suspension, dismiss ion, termination of any officer / staff employed by contractor. He shall have taken prior permission to employ or to terminate his personals.

- No watch and ward, safety insurance, security, storage, housing accommodation etc. will be provided by EMPLOYER. This will be responsibility of contractor.

- Consumable items like rubber bush, graphite packing, rubber sheet, nut-bolts, material require for cleaning and house keeping etc. are to be brought by the contractor.

- Electricity required for operation & maintenances of the pump station  will be provided by EMPLOYER. The contractor should provide all other consumables like pipes, specials jointing materials Diesel for vehicles etc. All the formalities to all Government authorities for factory, Electrical, TNPCB etc. for having NOC, water consent, Hazard waste concern, approval etc. shall be done by the contractor.

- Monitoring should be done as per guideline given by Engineer. Contractor has to maintain properly and if he will be penalized for not abiding statutoary requirements, all expenditure incurred for the same like, suite fee, court fee, case fee, or the penalty as decided by Engineer of EMPLOYER and penalty charged by State Government/Local Body will be charged to contractor and deducted from his bills, S.D etc.

- No equipment shall remain ideal or un-attended or damaged for the period of 3 days. If any equipment is not repaired, rectified and or replaced within 3 days, the contractor will be penalized with no limit at the rate of Rs. 2000/- per day delay per  each individual equipment of the pump station.

- The payment of O & M charges will be made as per the tender conditions. The other terms and condition described in these complete tender documents, wherever applicable shall remain unchanged. In case of any discrepancy the decision of Engineer will remain final & binding on the contractor.

- During Operation & Maintenance period, contractor has to supply all the spares, at his cost during preventive, major-minor breakdown, replacement and maintenance work. No extra payment will be made for such maintenance on any ground. The payment for the same will be made strictly as per tender document irrespective of the number of break down / minor, major repairs replacements. During the O & M contractor will have to enter annual maintenance agreement with Manufacturers of all major Mechanical Equipments like Sewer Cleaning Equipments, Non clog pumpsets, Screen arrangements, Odour control devices, Degritter, Panel Boards, Diesel Generators etc.

- Contractor will have to maintain required Power Factor as per TNEB rules and regulations. Incase penalty is levied by TNEB for not maintaining the Power Factor the same will be recovered from the contractor.

- Maintenance of Garden, Lawns, Plants, Bushes, Plantation of new Plants, Lawns etc. and feeding, gardening, cleaning etc. in Lift stations/Pumping stations is in the scope of the contractor. No separate payment will be made for the same.

- Operation and maintenance of all General facilities and utility services including all other components of work done under this contract.

- Operation and maintenance all instruments installed in the project. All repairs, replacements towards the entire instrumentation works during the O & M period shall be in the scope of contractor.

- Any other services required for smooth running of the scheme.

- The contractor shall also dispose off the sludge, screenings, grit and any other material, as per specifications and to the satisfaction of the Engineer. It is to be noted that all costs during the O&M period, excluding the cost of power  are to be borne by the contractor.

- The contractor shall provide on job training to the Local body  staff as per specifications.

- At the end of every year of operation & maintenance period, an assessment of the condition of the collection system has to be done by the contractor through third party inspection at his own cost and based on that assessment the contractor shall, at no extra cost to the EMPLOYER, repair and re-condition all the mechanical equipments in the concluding year of the O&M contract to a condition so that they are in running condition with regular preventive and recommended maintenance as per manufacturer's recommendations or as per CPHEEO manual.

- The contractor shall give or provide all necessary superintendence during the O&M and as long thereafter as the Engineer may consider necessary. Such superintendence shall be given by a competent person having adequate knowledge of the operation and Maintenance to be carried out (including the methods and techniques required), the hazards likely to be encountered and methods of preventing accident) as may be required for the satisfactory working of the entire pump station.

No labour below the age to 18 years shall be employed on the work.

List of staff is to be given by the agency to the Engineer and advance intimation to be given before deputing/removing any staff from site during the period of contract. Not more than one of the contractor's key staff shall be absent from the project site at any given time. In case it is necessary for more than one of the key personnel to be absent at a given time, the contractor shall provide replacement of equivalent or better qualifications. The CVs of such replacements shall be got approved from EMPLOYER in advance.

Engineer shall be authorized to direct the contracting agency to remove any or all staff employed on O&M of the collection system if in his opinion continued presence of such staff is detrimental to safety or proper O&M of the collection system. The contractor shall comply with such directions & post suitable substitute(s) thereof. Whenever the Engineer has to inform the contractor in writing that any person on the work is in his opinion unsatisfactory or/incompetent or unfaithful or dishonest, untruthful or disorderly or to be otherwise unsuitable/such person shall be discharged by the contractor from the work and shall not be employed again on it.

34) SAFETY/SECURITY

The contractor shall take all safety precautions under various Acts/Rules under central/State Govt. from time to time and he shall be responsible for safety of its staff and the consequences thereof. The contractor shall deploy round the clock security personnel at entrance of pump station’s premises and in the compound for the safety of the pump station and premises for the safety of the pump station, equipment and personnel during this period.The contractor is expected to follow all the applicable occupational health and safety norms as per applicable statutory standards.

Hoisting machinery- All workmen, gang-labor, operator, workers, supervisors involved in signaling, lashing and guidance maneuvering should be provided with pertinent safety gear and protection such as helmets, gloves, work overalls, steel toed boots, goggles and other gear as pertinent.

Risk of flooding-If working near water bodies  the contractor should follow the pertinent authorities warning such as weather fore casts,flash floods etc., as per directions of the meteorology department or competent authorities.

35) Responsibility for damages

The care of the whole of the permanent works shall remain with the contractor who shall be responsible for all accidents or damages from whatever cause arising and chargeable for any thing that may be stolen, removed destroyed or damaged to whomsoever belonging and also for making good all defects and damages to the said works or to any property adjoining or any cause whatever, whether such damage or defects were occasioned by the negligence of the contractor or not or may be or might have been discovered during the progress to be known after the completion whereof or whether payment may wholly or partially have been made.

Adequate safety precautions against fire, flooding, lightening, electrical shocks, accident due to moving/non-moving heavy/light equipments shall be strictly observed by the contractor at his own cost. Suitable safety measures like gumboots, gloves, safety belts, ladders, safety lamps, gas masks, Oxygen apparatus, insulated tools, alarms etc. shall be provided by the contractor. Necessary medical first aid kit shall be made available all the time. In absence of observance of above safety precautions, the contractor shall be responsible for any unforeseen loss of the equipments or persons dealing with it. Special care shall be taken by the contractor while carrying out the work in sewage gas zone. Any incidence of human life or accident will be totally contractor's responsibility.

The contractor shall ensure that the staff employed takes all necessary precautions while carrying out the work either in shift duties or any general shift as per Indian Electricity Rules/Factory Act/CPHEEO Manual, or manufacturer's special instruction for safety / gas handling. The staff should use Gas masks, Oxygen apparatus, Gum Boots, Safety Belts and Safety Lamps, etc. while carrying out the work in Bar Screens, sumps etc.

The contractor will make arrangement for all necessary safety equipments for persons working in the project as per Factory Act/Safety Rules. In the event of any accident on or off site, in which the contractor or his personnel are involved, in which an injury occurs to any person whether directly concerned with the project or a third party, the contractor shall inform EMPLOYER within 24 hrs. of the occurrence of the event. The pump station will be open to local/state/central agencies for verification of safety/emission/acts compliance.

During night hours, the main gate should be locked. However, shift duty staff should be alert and open the gate during surprise checking of EMPLOYER staff or any other Government Authorities or his nominee without any wait. Only bona-fide persons be allowed in the pump station premises being a prohibited area. Smoking and drinking are prohibited in the pump station. The staff engaged shall wear common uniform with name plate indicating name and designation during duty hours.

36)REPORTING

The Contractor will prepare daily and monthly reports (in EMPLOYER format) of pumping/treatment and project performance and submit to the Engineer and will assist the department in preparing the necessary documents for their purpose and record as per proforma given from time to time. The reports shall contain, inter-alia, the following:

.

              - A description of the maintenance work carried out in the reporting period.

- A report on major failures, if any, their causes and remedial actions taken.

- Sludge quantity (daily basis) in the reporting period.

- Power and chemicals consumed in the reporting period.

- An inventory of the chemicals and spare parts available at the end of the reporting Period.

- O&M staff deployed by the contractor during the reporting period.

- Any major repair works, if any.

Contractor is required to maintain separate register/computerized records at all sites of following information:

- Pumping register

- Working hours register

- Electric break down register

- Maintenance register

- Staff attendance register

- Equipment breakdown, repair record and extent of repair

- Diesel Generator operating and using register.

37) Site Order Book

Site order Book shall be kept by the Engineer  at the pump station site. Orders entered in this Book by the Engineer or his authorized representative shall be held to have been formally communicated to the contractor. The Engineer or his authorized representative shall sign each order as it is entered and will hand over the duplicate to the contractor or his agent, who shall sign the original in acknowledgment of having received the order.

38) Record Keeping

Running Records are required to be kept for various operating machines such as Mechanical Screens, Mechanical Grit Removers, Pumps, Motors, Scrapers, etc. as maintained by the operators and kept at Control Room or duty room of the operators that is closer to the location of the machines.

The record with respect to flow shall be maintained by operators. The operator passes the daily log sheet to the project Manager on the subsequent day duly signed in the first shift. All operators shall be responsible to fill up their part of observations and calculations. The project Manager shall verify the daily record as well as the calculations and shall be responsible to generate further data using these.

It is pertinent to mention that there shall be a requirement of drawing site-specific procedures and formats / forms for keeping records. This shall be the responsibility of the project manager.

39) OPERATION

In case, the motor or any other equipment is burnt or damage due to negligence of the contractor or due to faulty operation it shall be sole responsibility of the Contractor to rewind/replace/repair it as per standards of the equipment free of cost. In case of any fault in operation and performance of the pump station, contractor or his staff at duty will immediately report to the Engineer about it.

The Contractor shall run the pumping unit after ensuring proper voltage. He shall also record all the power failures and voltage in daily log sheet. He will bring into the notice of power supply agency as well as control room and Departmental Engineer about the break down/power failure. He will also get the electricity restored simultaneously.

Any dispute with the workmen shall be contractor’s responsibility as per Labour Laws/Govt. Rules and Regulations. In no way the department shall be responsible for the disputes between them.

The contractor shall follow the rules and regulations as per Factory Act as it is applicable.

The contractor shall arrange all necessary required tools, tackles and instruments in advance for proper operation and maintenance of the entire pump station.

The contractor shall operate and maintain all (E&M) equipment as per the recommendations of the respective equipment manufacturer. He shall further maintain and operate the pump station, as per CPHEEO manual to obtain the treated effluent results as per approved norms specified in this document elsewhere along with the Technical Bid. The contractor shall be free to follow manufactures manual in this regard. However in case of any doubt, the Employer. shall refer to best of the above standards and the contractor shall be bound to carry out the works accordingly.

The floating material/scum should be collected in bins and dispose the same in open pits away from the pump station, machinery which should be dried and disposed off regularly at a location outside the pump station and approved by statutory authority. During rainy season, this should be buried after using lime.

The screened material, grit and the dried sludge cake from the centrifuge should be collected in trailers, trucks or tractor and the same should be disposed off at Corporation Compost yard. away from the pump station on his own.

The Tenderers shall know all Central/State Government/ Semi-Government/Local Bodies rules regulations to this contract without any excuse. Gas coming out of sewage is hazardous containing Methane, CO, CO2 and H2s etc. Therefore, necessary precaution and measures are to be taken in regard to human life and installations.

40)MAINTENANCE

Every part of the works and all the materials to be used therein shall be subjected to such tests from time to time during the execution of the work as the Engineer may direct and the whole of such tests shall in all cases be made at the contractor’s sole expense.

The work shall be carried on and completed under the exclusive control direction and supervision and to the satisfaction of the Engineer. The Engineer shall likewise have full power to reject or condemn any work or material that he may deem unsuitable. In case of any work or material being rejected by the Engineer, the contractor shall immediately remove and replace the same to the satisfaction of the Engineer or the Engineer shall have full powers to get the same removed and replaced and deduct the expenditure incurred in the process from any amount due or that may become due to the contractor.

The contractor shall use only the original and genuine spares of the original equipment as per recommendations given in the maintenance booklet of the manufactures/as per directions of the Engineer. Adequate stock of such spares is to be maintained by the contractor. Test certificate of manufacturer is required for bearings along with supplies. Test certificate of all major equipment will be submitted from the manufacturer.

If any material brought upon the site of works or to the places where any Operations have been or are being carried out in connection with or for the purpose of the works, be in the judgment of the Engineer, of an inferior or improper description or improper be used in the works, the said materials or workmanship shall where required by the said officer be removed or amended by the contractor forthwith or within such period for every breach by the contractor in this clause, the Engineer is hereby authorized to remove or cause to be removed the materials and workmanship so objected to or any part thereof and replace the same with such other materials and workmanship as shall be satisfactory to him and there upon the contractor shall on demand repay to the Board the expenses incurred there by or to which the board may be put or be liable in connection therewith, the amount thereof to be certified by the Engineer whose certificate shall be final.

He shall be responsible for civil maintenance of buildings and roads changing of broken glasses, white washing and painting every two years and watering of lawns/plants within the pump station premises.

The contractor shall also be responsible to maintain cleanliness in around the pump station including machineries, disposal of floatings removed from the Bar Screens/reactors, etc. Grit and other unwanted material.

All the steel structures and machines installed in open areas should be painted after every monsoon period after cleaning the surface as per the instructions of the Engineer.

Entire pump station including all civil structures, mechanical equipments, HT panel and Transformers etc. shall be repainted after every 2 years as per original painting specifications.

Surface drains shall be cleaned every year before start of monsoon.

All leakages should be attended promptly to avoid any nuisance etc. Chokages should be removed at once. All the valves/gates which are not used regularly should be operated at least once a week and make sure that they are properly lubricated /greased.

All safety valves should be checked daily and ensure that they are working properly. In case of any fault the same should be attended immediately without any wait. The maintenance of the collection system shall be as per maintenance manuals of the manufacturer for all equipments. Contractor shall keep all the safety devices in working order.

The contractor should make sure that no unwanted material should float/grow in and around different units. In case it is found the same shall be removed /cleaned immediately. He shall also be responsible for cleaning/sweeping the pump station buildings inside and outside, roads, foot path etc.

During preventive/ breakdown maintenance, the contractor has to visit the unit/units as and when needed. The pumping units or other machineries required if any shall have to be arranged by the contractor at his own costs for completing the work. In case of battery operated auto system panels and also system alarm etc., batteries are required to be maintained and replaced as and when needed by the contractor.

The contractor has to make sure that proper fire extinguishers are used to cover any kind of fire during any miss-happening within the total boundary area including  machineries. The expiry period of refills of various fire extinguishers should be watched and maintained during the period of contract.

The contractor has to maintain all the toilets for proper use of the staff etc. In no case, in-sanitation conditions are developed. The contractor has to maintain minor repair in Civil structures, including replacement of sanitary items, glass pans etc. as and when needed.

The contractor shall not remove/shift any equipments/machinery even temporarily without written permission of the Engineer or authorized representative.

Though the contractor has to operate and maintain all the equipments/machineries, lighting (pump station area, boundary walls, gate lightening etc.) but the machine of the equipment under warranty should not be dismantled without prior permission of the Engineer. The list of such equipments (Under warranty), if any, will be given by the contractor.

POL (petrol/Diesel Oil & Lubricants) has to be arranged by the contractor as and when needed as per manufactures recommendations for periodical maintenance of entire pump station. The Department will not provide such items.

The contractor shall have to carry out periodical testing of the installations/equipments as per CPHEEO manual and I.E. Rules as amended up to date and shall have to maintain complete record in the maintenance register. The contractor has to provide necessary protection systems wherever necessary including alarms and fire extinguishers.

The Employer will be at liberty to post its staff for surveillance/ inspection at the pump station along with access to all units, control room and records, log books, MIS (Management Information system), data etc. round the clock as required. The logbooks and attested by the staff from authorized EMPLOYER Officials and this record shall be open for further inspection/checking by EMPLOYER and all other Government Agencies CPCB/TNPCB etc. for further action/improvements/rectifications. The staff in each shift shall mark their attendance on the log sheet individually. The equipments covered under the above contract shall be totally attended by the contractor including any 'Trouble Shooting' to ensure smooth and trouble free operation.

In case of major repair due to normal wear and tear/break down, the contractor should bring the same to the notice of the Engineer immediately and necessary measures for its repair should be taken simultaneously. Breakdown, all repairs of any kind are to be attended by the contractor. Any unit/equipment being irreparable in the opinion of the Engineer will be replaced by the contractor at no cost to EMPLOYER. During 5 years O & M period, the machinery/media to be replaced from time to time as per manufacturer's recommendations/CPHEEO manual.

All relays and HT equipments shall be calibrated and tested atleast once a year and the report shall be submitted to the Engineer.

The contractor shall give his telephone no., contact addresses, etc. to the EMPLOYER as well as shift duty shift to contact him during emergency/odd hours etc.

The contractor will be responsible to carry day to day as well as periodic maintenance, necessary to ensure smooth and efficient performance/running of all equipments instruments installed at the pump station.

He shall be responsible for maintenance/replacement of street light poles and light etc. also. All the pump station, building land, Sewage treated/untreated/sludge, etc. shall remain the property of EMPLOYER.

Oil & Grease Schedule

Routine & preventive maintenance of electrical /Mechanical/ hydraulic/ machines & equipments is to be carried out as per the operation & maintenance manual. Minimum oil & grease requirement for one year Operation & maintenance of the Pump station to be procured by the Contractor well in advance.

41)Routine, Preventive, Minor & Major maintenance of all Civil, Electrical, Mechanical, hydraulic machines & equipments of the pump station.

The contractor should prepare schedule of daily maintenance & preventive maintenance of all the equipments & machineries operated & run by him in the premises of the Lift/pumping station and sewer network. The schedule should be as per the guidelines mentioned in the tender &as per the O& M manual.

The scope covers Routine, Preventive, Minor & Major maintenance of all major minor equipments, and machines in the Pump station like Screens, Grit Removal Mechanism, Channel gates, Sludge pumps,  etc.

The scope also covers Routine, Preventive, Minor & Major maintenance of all the instrumentation system installed like PLC, Actuators, Flow meters level indicators etc.

The Contractor should also carry out Routine, Preventive, Minor & Major maintenance of all major minor electrical equipments like Electrical Panels, Switch Gears, Power Cables, Control cables, Changeover switches DG set etc so as to ensure uninterrupted round the clock operation of the Pump station.

The Contractor should maintain all civil structures including Pump room, Staff quarters,Storm Drains, fencing etc in a neat manner. He should maintain all civil structures of the pump station sturdy to complete the natural/designed lifetime.

The contractor should carry out the safety audit of the pump station &obtain necessary certificate from the competent authorities.

This item includes all types of Routine, Preventive, Minor & Major maintenance of all Civil, Electrical, Mechanical, hydraulic machines &equipments of the pump station covering supply erection test & trial run of the part/machine to be repaired/replaced with material &labour expenses, necessary hardware’s, sundry materials, lubricant oils, power oils, grease other materials plus machining charges etc.

The contractor should procure all the spares required for all types of maintenances in advance. The part/equipment/machine to be repaired /replaced should be as per the EMPLOYER approved list & as per the O& M manual or as per the existing manufacturer’s brand.

41)  RELEASE OF HAZARDOUS SUBSTANCES OR HAZARDOUS WASTE

The Contractor, after first notifying the TNPCB shall be responsible for fulfilling all requirements associated with any release of any substance into the environment (form the facility or the site) as required by Applicable law or by any Legal Entitlement including but not limit to the notification or reporting of releases / Hazardous substances or Hazardous Waste. The Contractor shall prepare a memorandum evidence such notification or reporting and provide copies thereof to the Board, along with any documents provided to the relevant regulatory agency regarding such release.

The contractor shall process and obtain the clearance of all such agencies as required for the purpose, including all clearances during 5 years O&M period. He shall be fully responsible to comply with all requirements of Laws including hazardous substances, emission standards for air, discharge standards for effluent oil, sub-soil pollution.

The contracting agency shall not release any hazardous/toxic materials inside the premises.

42)OPERATION AND MAINTENANCE MANUAL

- The contractor shall prepare a detailed program (referred to as O&M Manual) covering the operation and maintenance of the collection system as a whole. Notwithstanding the program submitted and approved, the Contractor is deemed to have tendered for and covered in his price, the responsibility for operating and maintaining the pump station for the full period of the contract, thereafter handing it over as specified.

- The contractor shall provide 3 copies of draft O&M Manual  to the EMPLOYER, at the time of  the commissioning of the project and on approval of draft, 10 copies of operation &maintenance manual shall be supplied by the contractor.

- The O&M Manual shall include  the daily, weekly, monthly, quarterly, half yearly and annual checks and remedies if necessary to be performed for effective operation of the pump station, elaborate detail, all operating and maintenance procedures and policies which are required, advisable and / or necessary for the Facility to achieve full compliance with the operational guarantees and to achieve maintenance and repair standard for the Facility which will ensure compliance with the maintenance specifications.  The O&M manual shall include interalia full explanation of all  procedures and processes.

- Without limiting the generality of the foregoing the O&M Manual shall include descriptions, procedures and shall comply with the requirements, set forth in the provisions of the Bid Documents.

- The draft of the O&M Manual shall be subject to the review and approval of EMPLOYER, which shall have the right to make any changes and revisions to the O&M Manual as it may deem appropriate. The Contractor shall revise such draft O&M Manual prior to the commencement of the O&M period.

- At the end of the construction period, the contractor shall revise the draft O&M Manual to reflect any updates, changes or revisions it deems appropriate, inter-alia based on its
experience and as necessary to reflect any modifications or adjustments to the pump station.
Without limiting the above, the contractor shall annually fully review, revise, update
and modify the draft O&M Manual as may be necessary or appropriate. Any revision
to the draft O&M Manual shall be subject to the review and approval of EMPLOYER.

- EMPLOYER shall have the right to require revisions to the draft O&M Manual as it may deem appropriate. The contractor shall prepare and submit to EMPLOYER, for its review  and approval, 30 days prior to the proposed date of commencement of O&M, a revised draft O&M  Manual which reflects all changes, revisions and modifications. The contractor shall prepare the O&M Manual, as approved by the Employer, prior to the start of O&M.

- During the term of this Agreement, the contractor shall promptly notify EMPLOYER of any revisions, additions or modifications which he, in his professional opinion, believes should be made to the O&M Manual, whether as a result of additional experience in operating and maintaining the Facility, changes in influent quality or volume, changes or modifications to any equipment, part, component or structure incorporated in the Facility. Such notification shall set forth the reason for the proposed revision. Any proposed revision shall be subject to the approval of the Employer. In addition, during the term of this Agreement, EMPLOYER shall have the right to require relevant changes, revisions, or additions to the O&M Manual as it, shall deem appropriate to ensure full compliance with the O&M Standards.

- The contractor shall submit 10 copies of the final O & M manual along with a soft copy in Microsoft Word Format.

43) TAKING OVER

The Collection system will be taken over by EMPLOYER on satisfactory completion of the Operation & Maintenance provided that

The equipment are in good, smooth running condition.

- In case of major repairs /replacement of equipment, the performance guarantee for such unit/equipment is extended by six months from the date of putting back in to satisfactory operation of such unit/equipment .In case such putting back is at the end of completion of operation & maintenance period.

- All records of operation & maintenance are handed over to EMPLOYER in proper condition.

- The Third Party Inspection of the pump station viz: Civil units, Mechanical units/equipments, Electrical units/equipments, instruments, &all other Major & minor units/machines has to be carried out & the defects unsatisfactory working performances of the equipments/ machines are to be corrected by the contractor at his own cost. The necessary Third Party inspection agency shall be appointed and charges paid by the Employer.

- The Contractor should repaint the pump station including all civil structures, mechanical, electrical equipments/ units /structures as per the tender specifications

In case taking over is delayed on account of contractor's failure, the operation & maintenance period will be extended further till it meets the requirement without any extra cost to EMPLOYER. The contractor will also be penalized for such delays.

XI  Reference to Specifications/ Code of Practice

(Latest edition / Version shall apply)

| Description | BIS No. |
| --- | --- |
| Sulphate Resistant Cement | 12330-1988 |
| 43 Grade Ordinary Portland Cement | 8112 - 1989 |
| Pozzolona Portland Cement | 1489 - 1991 |
| Hydrophobic Portland Cement | 8043 - 1978 |
| Rapid Hardening Portland Cement | 8041 - 1990` |
| Low Heat Portland Cement | 12600 - 1989 |
| Standard sand for testing of cement | 650 – 1966 |
| Methods of Test for Pozzolonic Materials | 1727 - 1967 |
| Methods of sampling and test for water & waste water (Physical & Chemical) | 3025 - 1984 (Part I to 37) |
| Methods of Sampling hydraulic Cement | 3535 - 1986 |
| Methods of Physical tests for hydraulic cement | 4031 - 1988 (1 to 14) |
| Methods of chemical analysis of hydraulic cement | 4032 - 1985 |
| Aggregates coarse & Fine from Natural resources for concrete | 383 – 1970 4082/1977 |
| Sand for Masonry Mortar | 2116 - 1965 1542 / 1977 |
| Methods of tests for aggregates for concrete | 2386 - 1963 (Part 1 to 8) |
| Part I - Particle size and shape | 2386 - 1963 (Part-I) |
| Part - II - Estimation of deleterious Materials & Organic impurities | 2386 - 1963 (Part - II) |
| Part III – Soundness | 2386 - 1963 (Part - III) |
| Methods of sampling of aggregates for concrete | 2340 - 1986 |
| Specifications for test sieves Part I - Wire cloth test Sieves | 460 – 1978 (part - I) |
| Common Burnt clay building bricks | 1077 - 1976 |
| Mild Steel and Medium tensile steel bars and hard | 432 – 1982 |
| Drawn steel wire, concrete reinforcement, Part I Mild Steel & Medium Tensile Steel Bars Part II Hard drawn steel wire |  |
| High Strength deformed steel bars and wires for Concrete reinforcement | 1786 - 1985 |
| High Tensile Steel for PSC Pipes | 1784 - 1986 (Part I) |
| Bending and flexing of bars for concrete reinforcement | 2502 - 1969 |
| Recommendation for detailing of reinforcement In reinforced concrete works | 5525 - 1969 |
| Methods for tensile testing steel wire | 1521 - 1972 |
| Methods of test for determining modulus of elasticity | 2854 - 1964 |
| Glossary of terms relating to cement concrete | 6461 - 1972 (Part 1 to 12) |
| Methods of test for strength of concrete | 516 – 1959 |
| Methods of sampling and analysis of concrete | 1990 - 1959 |
| Methods of testing bond in reinforced concrete pull out test | 2770 -1967 |

| Description | BIS No. |
| --- | --- |
| Methods of test for permeability of cement Mortar and concrete | 3085 - 1965 |
| Methods of test for splitting tensile strength of concrete cylinders | 5816 - 1970 |
| Methods of tests for determining setting time of concrete by penetration resistance | 8142 - 1976 |
| Code of practice for construction of Pile foundations (concrete piles) Driven cast-in-situ concrete piles Bored cast -in-situ piles Driven pre-cast concrete piles Bored pre-cast concrete piles | 2911 (Part (I) Sec 1 - 1979 Sec 2 - 1979 Sec 3 - 1979 Sec 4 - 1984 |
| Code of practice for construction of raft foundation | 2950 - 1981 |
| Design Aids for reinforced concrete | SP 16 - 1980 |
| Explanatory Hand Book on codes for earthwork Engineering | SP 22 - 1982 |
| Explanatory Hand Book on IS Codea 456 – 1976 | SP 24- 1983 |
| Hand Book on causes and prevention of cracks in buildings | SP 25 - 1984 |
| Hand book on concrete reinforcement and detailing | SP 34 –1987 |
| Brick Masonry | 2212 –1962 |
| Construction of Stone Masonry | 1957 – 1967 |
| Asbestos cement pressure pipes | 1592 – 1989 |
| Concrete pipes with and without reinforcement | 458 – 1988 |
| P.S.C. pipes (including fittings) | 784 – 1978 |
| Methods of tests for concrete pipes | 458 – 1988 3597 – 1985 |
| Materials for M.S. Specials | 226 – 1976 & 2062 – 1980 |
| Specification for M.S. Specials for P.S.C. Pipes |  |
| Specification for Steel cylinders reinforced concrete pipes | 1916 – 1989 |
| Methods of tests for concrete pipes | 3597 - 1985 |
| Special for steel cylinders reinforced concrete pipes | 3597 – 1985 |
| Cast iron specials for asbestos cement pressure Pipes for water, gas & Sewage | 5531 – 1988 |
| Methods of test for asbestos cement products | 5913 – 1989 |
| Dimensional requirements of rubber sealing ring for CID joints in asbestos cement pipe | 10292 – 1988 |
| Centrifugally Cast (Spun) Iron pressure pipes for Water, gas and sewage including fittings | 1536 – 1989 |
| Specification for Centrifugally Cast (Spun) D.I. Pipes for Water, Gas and Sewage | 8329 – 1990 |
| D.I. fittings for pipes for water gas & Sewage | 9523 - 1980 |
| Dimensional requirements of rubber gaskets for mechanical joints and push on joints for the use with C.I., D.I. Pipes | 12820 - 1986 |

| Description | BIS No. |
| --- | --- |
| C.I. Specials for Mechanical and push on flexible joints for pressure pipe lines for water, gas & sewage | 13382 - 1992 |
| Horizontally cast iron double flanged pipes for water, Gas and Sewage | 7181 - 1986 |
| Cast iron fittings for pressure pipes for water, gas and sewage | 1538 - 1976 (Part 1 to 24) |
| Cast iron detachable joints for use with asbestos cement pressure pipes | 8794 – 1988 |
| Rubber rings for jointing C.I. pipes, RCC Pipes & AC Pipes | 5382 – 1969 |
| Rubber rings for jointing P.S.C. Pipes | 5382 – 1985 |
| Rubber rings for jointing AC pipes with AC couplings | 10292 – 1985 |
| Hemp yarn | 6587 – 1966 |
| Rubber insertion to be used in jointing CIDF Pipes | 638 – 1979 |
| Bolts & Nuts to be used in jointing CIDF Pipes | 1363 – 1967 |
| Unplasticized PVC Pipes for potable water supplies | 4985 – 1988 |
| Injection moulded PVC socket fittings with Solvent cement joints for water supplies | - – 1987 (Part I to 8) |
| Fabricated PVC fittings for potable water supplies | 10124 – 1988 (Part I to 13) |
| Methods of test for unplasticized PVC pipes for potable water supplies | 12235 – 1986 (Part I to 11) |
| Sluice valves for water works purposes (50 to 300mm Dia size) | 780 – 1984 |
| Sluice valves for water works purposes 300 to 1200mm Dia size) | 2906 – 1984 |
| Surface boxes for sluice valves | 3950 – 1979 |
| Machine-hole covers for sluice valves | 1726 – 1974 |
| Laying of Asbestos Cement Pressures Pipes | 6530 – 1972 |
| Laying of concrete Pipes | 783 – 1985 |
| Laying of Cast - Iron Pipes | 3114 – 1985 |
| Laying of PSC Pipes | 126 of APSS & 783 – 1985 |
| Laying of DI Pipes | 12288 – 1987 |
| Laying and Jointing of unplasticized PVC Pipes | 7634 – 1975 (Part 3) |
| Batch type concrete mixer | 1791 – 1968 |
| Sheep foot roller | 4616 – 1968 |
| Safety code for excavation works | 3764 – 1966 |
| Safety code for scaffolds and ladders Part I – Scaffolders Part II – Ladders | 3696 – 1966 (Part I) 3696 – 1966 (Part II) |

| Description | BIS No. |
| --- | --- |
| Safety code for piling and other deep foundations | 5121 – 1969 |
| Safety code for working with construction machinery | 7293 – 1974 |
| Tamil Nadu Building Practice | Volume – I Volume – II |
| Government of India Manual on Water Supply and Treatment | May 1999 (Revised) |
| Gravel for packing | 4091 – 1967 |
| Hard drawn steel wire | 1785 – 1983 (Part I and II) |
| Structural Steel | 226 – 1975 |
| Hand rolled mils steel for concrete | 1139 – 1966 |
| Hard drawn Steel Wire | 1566 – 1982 |
| American Society for Testing of materials |  |
| British Standard | 2494 – 1955 Part I |
| Welding Electrodes | 814 – 1970 |
| Steel Sheets | 225 – 1975 |
| Guniting | 7322 – 1994 |
| Welding Joints | 3589 – 1966 and 2041 – 1962 |
| Tensile Test | 223 – 1950 |
| Mechanical and Electrical works |  |
| Turbine Pump | 1710 – 1972 |
| Submersible Pump | 8030 – 1976 |
| Submersible Motor | 9283 – 1979 |
| Earthing | 3043 – 1966 |
| Transformer | 1180 – part 1 2014 |
| Generator | 2253 – 4722 |
| HDPE Pipes | 4984 - 1995 |
| DWC Pipes | 16098(pt 2)/EN 13476-3 |
| DWC pipe elastometric O ring | IS 5382 |

XII  Environmental Management Plan for UGSS projects.

Environmental Monitoring Programme

Regular monitoring in a systematic and standardized manner helps in assessment of current environment and provides information on operational performance of installed pollution control facility. During construction Constant supervision over the site to control the movement of materials and noise disturbances are monitored.

The environmental monitoring will be required for the construction and operational phases. The main objectives of environmental monitoring area:

- To assess the changes in environmental conditions,

- To monitor the effective implementation of mitigation measures,

- Warn significant deteriorations in environmental quality for further prevention action.

The environmental monitoring plan would be as indicated in the table below:

Table 1: Pre-Construction andConstruction Stage Environmental Monitoring Plan

| Monitoring field | Monitoring location | Monitoring parameters | Frequency | Responsibility | Cost and Source of Funds |
| --- | --- | --- | --- | --- | --- |
| Baseline water quality of receiving water body (Selvachinthamani Tank and downstream Periyakulam Tank, Noyyal River) | 6 points (2 samples from each tank& from Noyyal River) | pH, TDS, TSS, DO, BOD, COD, E-coli, Total coliform, Nitrate, Total Phosphates, Oil & grease, Total hardness, Sulphate, Fluoride, Chloride, Ammonia, Aluminum, Manganese, Iron, Zinc, Nickel, Magnesium, Phenolic compounds, Chromium, Arsenic, Mercury, Cadmium, Lead, Pesticides | Twice during detailed design phase (Pre monsoon and post monsoon during design phase) | DBOT Contractor | Cost for implementation of monitoring measures responsibility of DB contractor (6 samples x 8000 per sample = 48,000) |
| Baseline sediment quality in receiving water bodies (Periyakulam Tank& Noyyal River) | 2 points (Periyakulam Tank& Noyyal River) | EC, pH, calcium, magnesium, % of total organic matter, Total organic carbon, N, P, K, Aluminum, fecal coliform, As, Cu, Cd, Cr, Pb, Fe, Mn, Hg, Zn, Ni. | Twice during detailed design phase(Pre monsoon and post monsoon during design phase) | DBOT Contractor | Cost for implementation of monitoring measures responsibility of DBOT contractor (4 samples x 10000 per sample = 40,000) |
| Construction disturbances, nuisances, public and worker safety, | All work sites | Implementation of construction stage EMP including dust control, noise control, traffic management, and safety measures during controlled blasting.Site inspection checklist to review implementation is appended at Appendix 7 | Weekly during construction | Supervising staff and safeguards specialists of CMSC | Staff and consultant costs are part of incremental administration costs |
| Ambient air quality | 5 locations (STP and4 monitoring locations 50 m downwind direction near sewer and pumping station work sites in the city); | - PM10, PM2.5 NO2, SO2, CO | Once before start of construction Quarterly (yearly 4-times) during construction (3year construction period | ConstructionContractor | Cost for implementation of monitoring measures responsibility of contractor (65 samples x 5000 per sample = 325,000) |
| Ambient noise | 5 locations (STP and 4 monitoring locations near sewer and pumping station work sites in the city); | - Day time and night time noise levels | Once before start of construction Quarterly (yearly 4-times) during construction (3year construction period) | Construction Contractor | Cost for implementation of monitoring measures responsibility of contractor (65 samples x 1500 per sample = 97,500) |
| Surface water quality | 2 locations (PeriyaKulam and Noyyal River at proposed STP discharge point) | - pH, Oil and grease, Cl, F, NO3, TC, FC, Hardness, Turbidity BOD, COD, DO, Total Alkalnity | Once before start of construction Half yearly during construction (3year construction period) | Construction Contractor | Cost for implementation of monitoring measures responsibility of contractor (12samples x 4000 per sample = 48,000) |

Table 2: Operation Stage Environmental Monitoring Plan

| Monitoring field | Monitoring location | Monitoring parameters | Frequency | Respon-sibility | Cost and Source of Funds |
| --- | --- | --- | --- | --- | --- |
| Monitoring of treated wastewater quality from STP | Inlet and outlet of STP | Parameters as specified by TNPCB in the consent/ disposal standards notified for STPs. | Monthly Once | CCMC | CCMC Operating Cost |
| Odor monitoring at STP | 2 points (downwind direction) with at STP boundary and at boundary near Residential area | Hydrogen Sulphide (H2S) | Half yearly (yearly twice) and as and when based on public complaints (throughout the operation phase) | CCMC | O&M Costs |
| Ambient noise | 2 location s (downwind direction) with at STP boundary and at boundary with near Residential area | Day time and night time noise levels | Monthly once during operation | VCMC | O&M Costs |
| River water quality at disposal point | Noyyal River disposal point, (downstream and upstream) | pH, Cl, F, NO3, TC, FC, Hardness, Turbidity BOD, COD, DO, Total Alkalinity, heavy metals and pesticides | Baseline monitoring prior to start of commissioning Monthly once during operation Yearly twice during operation (pre and post monsoon) | CCMC | O and M costs (water quality will be tested at the internal laboratory part of STP) |
| Odor monitoring at pumping stations | 3 points (downwind direction) at all pumping stations: near inlet/suction well; outside the pumping station and at nearest house | Hydrogen sulphide (H2S) | Periodical (throughout the operation phase) | CCMC | Handheld H2S meters to be procured as part of the project and operated by operating staff |
| Odor monitoring at lifting stations | 2 points (downwind direction) at all lifting stations: near suction well and at nearest house | Hydrogen sulphide (H2S) in ambient air | Periodical (throughout the operation phase) | CCMC | Handheld H2S meters to be procured as part of the project and operated by operating staff |
| Sludge quality and suitability as manure | STP | Analysis for concentration of heavy metals and confirm that value are within the limits for use as compost | Start of operation and Yearly once | CCMC | O and M costs (testing to be done at an accredited external laboratory) |

XIII  Resettlement Plan

Underground Sewerage System for Coimbatore Corporation Added Areas of Kavundampalayam and  Thudiyalur Wards 1(part), 2 to 9 and 43(part)-ZONE VII,

The project component consist of  3 no's  of  Lifting Stations, 12 Nos of Lift Machine-holes  and 2 Nos of Pumping Stations. The sites do not belong to any private ownerships and resettlement plan does not applicable to the above sites of this project.

XIV. MATERIAL TESTING SAMPLING PROCEDURE

TAMILNADU WATER SUPPLY AND DRAINAGE BOARD

SAMPLING PROCEDURES AND TESTING CAHRGES FOR MATERIAL QUALITY TEST

As per Managing Director ,TWAD Lr. No. F. 7161/Testing Charges/ LAB/ AEE/SQMS/ 2019

Dt 6.12.2019

| Sl No. | Name of material / tests to be conducted | Testing Charges (including Service Tax now in force). | BIS No. (for Reference) | Required Sample |
| --- | --- | --- | --- | --- |
| 1 | AC Pipe upto 400 mm (Hydraulic and Transverse crushing strength ) | Rs. 1,530 | BIS 1592:1989 | One full length of AC pipe with clearly visible brand name and batch number. Two set of CID Joints with bolt and nuts, "O" Ring ( six nos.), "O" ring size 5-10-15-20 three nos,. The sample collecting officer should authenticate the sample with permanent marker pen at site. The AC pipe may be taken back after completion of tests. |
| 2 | Steel ( Unit weight, Proof stress, Tensile strength and % of elongation) | Rs. 2,000 | BIS 1786:1985 | 3 Nos. Steel rod of 1.00 m length for each size (straight, true to axis) a)BrandName b) Size and c) ISI Mark valid CML No. d) Type and Grade Fe415 & Fe 500 should be clearly visible on the sample. e) The sample should be wrapped by brown tape and should be authenticated with Name of Scheme/ ISI CML No by the sample collecting Officer using permanent marker. |
| 3 | Cement (Initial and Final setting time, Finess, 3rd & 7th day compressive strength) | Rs. 5,100 | OPC 43Gr. BIS 8112:1991 OPC53Gr. BIS 12269:1991 | One sealed( 50 Kg full bag (OPC 43 / 53 Gr) with following detail clearly printed on the bag - a) Manufacturer's name and Trade mark b) Nature of cement/Grade c) BIS Certificate mark and CML No. d) Batch No : Week(within current three weeks) / Month / Year (Clearly Visible & Legible) The sample collecting Officer should authenticate the sample over cement bag with permanent marker pen at site. The cement bag may be taken back from the laboratory after completion of test. |
| 4 | Sand ( Fine aggregate)- Sieve analysis, Grading and Specific gravity. | Rs. 1,400 | BIS 383:1970 | Sand Qty- about 1/2 Cement bag(15Kg)- a) Name of work b) Date of collection / Place c) Signature on the bag for authentication with permanent marker. |
| 5 | Coarse aggregate- 40 mm only. (Sieve analysis and Specific gravity ) | Rs. 1,400 | BIS 383:1970 | Coarse aggregate – 40mm Qty - about 15 kg - a) Name of work b) Date of collection / Place c) Signature on the bag for authentication with permanent marker |
| 6 | Coarse aggregate- 20 mm ,12.5mm and 10mm ( Sieve analysis, Specific gravity and Crushing value ) | Rs. 2,300 | BIS 383:1970 | Coarse aggregate- 20mm, 12.5mm and 10mm Qty - about 15 kg - a) Name of work b) Date of collection / Place c) Signature on the bag for authentication with permanent marker |
| 7 | Concrete cubes (Compressive strength) | Rs. 1,400 | BIS 456:2000 | The Concrete cubes should have the following details marked by nail at the time of casting (should not be engraved at later stage) - a) Date of casting b) Grade of mix c) Identification mark (short form of component) d) The well casted cubes have to be handed over well before the due date for 7 days / 28 days testing, the date of testing should be reckoned inclusive of date of casting as per BIS. The size of cube should be 15cm x 15cm x15cm. At least minimum 3 cubes (1set) should be sent for each test. For 1 to 5 cum vol of concrete - 1Set For 6 to 15 cum vol of concrete - 2Sets For 16 to 30 cum vol of concrete - 3Sets For 31 to 50 cum vol of concrete - 4Sets Signature on the cube by sampling officer with permanent marker pen for authentication . |
| 8 | Hollow Blocks (Compressive strength ) | Rs. 1,200 | BIS 2185:1983 (Part I) BIS 383:1970 | Hollow blocks 3 Nos full size. The sample should be wrapped by brown tape and should be authenticated by sampling officer with permanent marker on it ( For at least one block) |
| 9 | Bricks ( Water absorption, Compressive strength and Efflorescence ) | Rs. 3,500 | BIS 3495:1992 BIS 1077:1992 | 15 Bricks with Brand name. The sample should be wrapped by brown tape and should be authenticated by sampling officer with permanent marker on it (for at least one brick). |
| 10 | Paver Blocks ( Water absorption and Compressive strength ) | Rs. 2,700 | BIS 15658:2006 | 12 Paver blocks with Brand name. The sample should be wrapped by brown tape and should be authenticated by sampling officer with permanent marker on it (for at least one Paver block). |
| 11 | Filter Media Sand - (Acid solubility, % of impurities, Loss of Ignition, Effective size and Uniformity coefficient ) | Rs. 3,500 | BIS 8419:1977 | Filter Media Sand – about 15 kg. a) Name of work b) Date of collection and Place c) Signature of the sampling officer on the bag for authentication with permanent marker. |
| 12 | Filter Media Pebbles - ( Acid solubility, % of impurities, Effective size and Uniformity coefficient) | Rs. 3,500 | BIS 8419:1977 | Filter Media Pebbles Up to 20 mm – Qty 15 kg. For 40 mm – Qty 20 kg Above 40 mm - Qty50 kg a) Name of work b) Date of collection and Place c) Signature of the sampling officer on the bag for authentication with permanent marker. |
| 13 | Unplasticized Polyvinyl Chloride Pipes - UPVC for Water Supply (Short term Hydrostatic pressure test, Impact strength test at 0 deg Centigrade, Density, Reversion test at 150 deg centigrade, Dimensions and wall thickness ) | Rs. 4,700 | BIS 4985:2000 | a) PVC Pipe 3 nos of 1.50m length (out of 3, 1 no with socket, 2 No with spigot from different pipes of same batch No.). b) The Make, ISI CML No. and Batch No., Size & class should be clearly legible and visible on pipes surface, third party test logo affix on socket pipe c) Name of the scheme, Field Engineer’s, Sample collection officer and contractor’s signature on all the three pipes surface with permanent marker pen. d) Five samples of 5 cm length taken from five different pipes of above same batch with authentication of the collection officer in all the samples with Batch number ( The samples may be cut in the spigot end of the pipe so that machine cutting end is visible at one end of the sample) |
| 14 | Unplasticized Non - Pressure Polyvinyl Chloride - UPVC-U Pipes for UGSS - (Short term Hydrostatic pressure test for pipe and joints, Impact strength test at 0 deg Centigrade, Reversion test at 150 deg centigrade, Vicat softening temp test, Dimensions and wall thickness ) | Rs. 4,700 | BIS 15328/2003 | a) PVC-U Pipes 3 nos of 1.50m length (without socket) and 3 nos of 0.60m length with socket. b) The Make, ISI CML No. and Batch No., Size & Nominal Ring Stiffness should be clearly legible and visible on pipes surface, third party test logo affix on socket pipe c) Name of the scheme, Field Engineer’s, Sample collection officer and contractor’s signature on all the three pipes surface with permanent marker pen. |
| 15 | Galvanized Iron - GI Pipe Upto 50 mm ( Dimensions, Unit weight, Bending test and Mass of Zinc coating ) 65 mm and above ( Dimensions, Unit weight, Flattening test and Mass of Zinc coating) | Rs. 4,500 | BIS 1239/1992 (Part I) | a) GI Pipe Upto 50 mm One piece of 1.2m length. For 65 mm and above one piece of 1.2m length. b) The Make with ISI CML No. Size & class Should be clearly legible and visible on the pipe surface. The sample collecting officers should authenticate all the samples with permanent marker pen at site. The straight pipe should be cut true to axis at least 30cm away from the threaded portion. c) Name of the scheme, Field Engineer’s, Sample collection officer and contractor’s signature on all the three pipes surface with permanent marker pen |
| 16 | Stoneware – SW pipe (Hydraulic test, Water absorption test, Acid and Alkali resistance test and Crushing strength test ) | Rs. 4,200 | BIS 651/2007 | Stoneware pipe 3 Full pipes with socket. a) Make, Batch no & size with third party test logo affix should be clearly legible and visible on the pipe surface. b) The sample collecting officers should authenticate on all pipes with permanent marker pen at site. c) Name of the scheme, Field Engineer’s, Sample collection officer and contractor’s signature on all the three pipes surface with permanent marker pen. Any damage in transit will liable for rejection. |
| 17 | M 30 Concrete Mix Design - | Rs. 23,800 | BIS 10262/2009 | Cement - 1 bag (OPC Grade) Sand - 4 bags Coarse Aggregate(12.5mm,20mm size) – 4 bags are required. For cement One sealed( 50 Kg full bag (OPC 43 / 53 Gr) with following detail clearly printed on the bag - a) Manufacturer's name and Trade mark b) Nature of cement/Grade c) BIS Certificate mark and CML No. d) Batch No : Week(within current three weeks) / Month / Year (Clearly Visible & Legible) The sample collecting Officer should authenticate the sample over cement bag with permanent marker pen. For Sand and Coarse Aggregate a) Name of work b) Date of collection / Place c) Signature on the bag for authentication with permanent marker pen |
| 18 | Ductile Iron - DI pipe for Water supply (Hydraulic Test, Dimensional Property, Coating) | Rs. 10,500/- (for 100 to 300mm Dia.) Rs.14,000 (For 350-600mm Dia.) | BIS 8329/2000 | a) Ductile Iron(DI) One Full length Ductile Iron S/S. pipe in standard length and sample of minimum 30 cm cut barrel pipe from spigot end of above same batch. b) Make, CML No. & Batch No. with third party test logo affix should be clearly, legible and visible on the pipe surface. c) Name of the scheme, Field Engineer’s, Sample collection officer and contractor’s signature with permanent marker pen inside pipe over cement mortar lining. |
| 19 | High Density Polyethylene-HDPE Pipe (PE100 grade) for Water supply(Density,MFI, Carbon Black Content,Hydraulic Test,Dimensioning, Carbon Dispersion,Reversion Test) | Rs. 19,600 | BIS 4984/1995 | a) HDPE Pipe(PE 100 grade) 3 Nos of 1.5m from standard length pipe. b) The Make, ISI CML No. and Batch No., Size & class should be clearly legible and visible on pipes surface, third party test logo affix on socket pipe c) Name of the scheme, Field Engineer’s, Sample collection officer and contractor’s signature on all the three pipes surface with permanent marker pen. |
| 20 | Double Wall Corrugated High Density Polyethylene-HDPE Pipe for UGSS (Name of test: Density,MFR, Carbon Black Content,Hydraulic Test,Dimensioning, Carbon Dispersion, Reversion Test) | Rs. 19,600 | BIS 16098/2 (2013) | a) Qty – DWC HDPE Pipe 3 Nos of 1.5m from standard length pipe. b) The Make, ISI CML No. and Batch No., Size & class should be clearly legible and visible on pipes surface, third party test logo affix on socket pipe c) Name of the scheme, Field Engineer’s, Sample collection officer and contractor’s signature on all the three pipes surface with permanent marker pen. |
| 21 | Electrical Cable | As given Below | BIS 10810 /1984 | Qty-Minimum 20 m length of cable to be collected |
| a | ELECTRICAL CABLES; PVC INSULATED CABLES | 1.5 sq.mm , 2.5 sq.mm, 4.00 sq.mm , 6.00 sq.mm , 10 sq.mm & 16.00 sq.mm - Rs 11900 per sample |  |  |
| b | PVC INSULATED ( HD ) CABLES UP TO 1100 V | 4.00 sq.mm to 35.00 sq.mm - - Rs 11900 50 sq.mm to 150.00 sq.mm - Rs 14700 , 185 sq.mm - Rs 16800 240 sq.mm - Rs 19600 and 300 & 400 sq.mm -Rs 25900 per sample |  |  |
| c | PVC INSULATED ( HD ) CABLES 3.3 KV UPTO & INCLUDING 11 KV | 3 C 240 sq.mm, 3 C 185 sq.mm 3 C 150 sq.mm 3 C 120 sq.mm Rs 19600 3 C 95 sq.mm , 3 C 70 sq.mm Rs 16800 per sample |  |  |
| d | XLPE Cable for voltages upto and including 1.1 KV | Rs. 16800/- up to 3 core for cables up to 95 sq.mm Rs. 3300/- for additional Core and for cables above 95 sq.mm & up to 240 sq.mm per sample |  |  |

Note: 18% GST Extra for the above testing charges

I .TESTING CHARGES

- The testing charges have to be paid in advance at first by the contractor at the time of handing over of samples.  The charges have to be paid by means of Demand Draft drawn in favour of specified designation communicated by concern laboratory.

As per Managing Director’s TWAD Board, Chennai Lr.No. F.7161/Testing Charges/SQMS/2013/Dt.02.12.2013 testing charges have to be refunded to the contractor on production of receipt however testing charges for failure sample by resample / replaced sample taken by inspection officer concerned should be borne by the contractor from his own cost.

- The sample should accompany with covering letter along with prescribed format (hard copy) duly filled details of sample, scheme, etc., with signature of field officer, sample collecting officer.

- One set of sample for any materials for two different contractors (Though same batch number) will not be accepted.

- If different contractors are using the same batch no (of any materials) separate samples should be collected by each contractor and to be got tested.

- If the contractor used already tested Batch No(PVC Pipe)in another scheme in which the requirement of the pipe below 250m,exemption may be granted for testing.

- If a second (check) sample as super check have to done by the inspecting officer’s (i.e. AEE (QATA) /EE /SE /CE /any inspection Officer) the contractor should permit them to take additional samples. However cost of such second testing will be borne by TWAD Board.

- The sample will be accepted and admitted for testing in the Laboratory only when the above conditions are fulfilled.

II FAILED SAMPLES

- In case of PVC Pipes, if it is fail in Impact test and still within the permissible limit to continue the test as per BIS, the additional sampling should be done by the higher Officers or QATA Engineer, from the same batch No. at site of work. The cost should be borne by the contractor only for proving its quality.

- If the sample collected by the field officers (AE, AEE, and EE) failed in the laboratory test, re- sampling (i.e same make and batch) should not be done as a matter of routine. However if the contractor feels that a second check for the same is required based on any specific reason the matter may be referred to the Superintending Engineer for taking a final decision, in such case Double sample have to be taken, with required testing charges which have to be borne by the concerned contractor only. Such things should be immediately informed to the Head office confidentially for taking further action. Further if the above resample fails in retesting also then the entire lot / batch should be rejected and removed from the site and the fact may be informed by certification to the Head Office (SQMS) by the concerned Executive Engineer. Moreover go for replaced sample by New Batch/Lot/Brand and also ensure the rejected materials are not used in any other works / Scheme also.

- The replaced sample (i.e new batch / Lot / New Brand) in lieu of the failed sample from the new lot arrival should be collected only by the AEE (QATA) of the territorial circle subject to the conditions on formation of certificate by the Executive Engineer concerned.

III Norms for Routine Sample Collection

- CEMENT & STEEL

i) One set of sample have to be taken for each and every name work as per IMIS entry of IPP/RWS schemes. Single sample does not holds good for many number of works clubbed together in single agreement by package tender.

ii) One set of sample have to be taken for each and every consignment for CWSS of  Rural / Urban/ Major Project/Stand alone.

iii) The validity of CML by BIS should be in alive for operative year of license.

- PIPES

UPVC Pipe for WS & U PVC-U Pipe for UGSS

i) If a contractor uses the same batch No. for different works,

One set of sample have to be taken for each and every name of work as per IMIS entry of IPP/RWS Schemes. Single sample does not holds good for many number of works clubbed together in single agreement by package tender.

ii) For CWSS of Rural//Urban/Major Project/Stand alone schemes one set of sample for every one lot reckoned as 1000 Nos of pipes/lot (i.e.6,000m) of same batch/brand is required subject to the production of copy of purchase bill  along with third party test certificate with test report in full shape should be produced compulsory.

iii) For more than 6,000 m, additional samples should be collected by inspection officers for every 6,000 m and as afore said documents should be attached.

iv) The validity of CML by BIS should be in alive for operative year of license.

- GALVANIZED IRON (GI) PIPE

One set of sample for every batch / CML of 500m length for RWS schemes. Exemption may be allowed for below 100m length to be used for minor works.

For CWSS of Rural /Urban/ Major project additional sample for every 500m should be collected by sample collection officer. Third party test certificate should be annexed as like for PVC Pipe.The validity of CML by BIS should be in alive for operative year of license.

- STONE WARE PIPE(SW)

One set of sample have to be taken for same batch of 3000m length should be collected. Additional sample should be collected for every 3000m length of same batch/brand. The copy of purchase bill along with bucca third party test certificate with test report in full shape should be produced compulsory.

- DUCTILE IRON PIPE (DI)

One set of sample have to be taken for same batch

For size upto 300mm : single sample for same batch upto 1200m   length(200Nos of full pipe). Additional sample of same batch should be collected for every 1200m(200 Nos) length.

For size from 300mm to 600mm : single sample for same batch upto 600m length (100Nos of full pipe). Additional sample of same batch should be collected for every 600m(100 Nos) length.

The validity of CML by BIS should be in alive for operative year of license.

NB:

- As per ground reality the sample should be collected at the site of work only by the sample collection officer duly after verifying the important documents as stipulated below.

i. For all Materials (Cement, Steel & all Pipes) the validity of CML by BIS should be in alive for operative year of license.

ii. For cement	: Grade & production Week, Month & Year

iii. For steel 		: Fe415/500, ISI Mark

iv. For Pipes		: Make, Size, Class, Batch No/Lot No., Third Party

inspection test certificate with test report

in full shape from the approved Third Party Agency.

- To avoid delay in receipt of sample for testing the following point have to be adhered scrupulously.

- Contradictory should be avoided between sample and format furnished both soft & hardcopy.

- The correct testing charges now in force have to be remitted in the form of Demand Draft to correct name of payee specified and communicated by concerned material quality testing laboratory with period of validity date as per banking account rules should be remitted.

- Any deviation of aforesaid terms and less payment will liable for rejection.

3.	Exemption may be allowed for testing the materials of lesser quantity in minor  works (ie) Anganwadies, PFs, Pump Room Kiosk and valve pit.