RAMANATHAPURAM  CWSS

SALIENT DETAILS

| 1. | Name of Scheme | : | CWSS to Ramanathapuram and 4 other Municipalities, 11 Town Panchayats and 3163 Rural Habitations in 18 Panchayat Unions in Ramanathapuram, Sivagangai and Pudukkottai Districts. |
| --- | --- | --- | --- |
| 2. | Admn. Approval No. and Date. | : | G.O.Ms.No. 146/MA & WS Dept./ Dt.01.12.2006 for Rs.616.00 crores. |
| 3. | Tech. Sanction No. and Date. | : | 1) Chief Engineer/SR / MDU No.21/2006-2007/ Dt.06.12.2006 for Rs.3850 Lakhs. – Stage I. 2) Chief Engineer/SR/MDU No.53/2006-2007/ Dt.19.02.2007 for Rs.59650 Lakhs – Stage II. |
|  | Revised Admn. Approval No. and Date as per Execution. | : | G.O.Ms.No. 119/MA & WS Dept./ Dt.07.08.2015 for Rs.671.592 crores. |

4.  FUNDS								 (Rs. In crore)

| Funding Agencies | TUFIDCO |  | NABARD | MNP | TOTAL |
| --- | --- | --- | --- | --- | --- |
|  | Mplty | T.P. |  |  |  |
| Funds Tie up for Urban Components | 191.15 | 90.86 | 0.00 | 0.00 | 282.01 |
| Funds Tie up for Rural Components | 0.00 | 0.00 | 273.12 | 60.87 | 333.99 |
| Total | 191.15 | 90.86 | 273.12 | 60.87 | 616.00 |

| 5. | Population benefited | : | Base year population (2006) .. 15.76 Lakhs. Ultimate population (2036) .. 19.76 Lakhs. |
| --- | --- | --- | --- |
| 6. | Pro- rate supply | : | Municipalities .. 70 lpcd. Town panchayats .. 50 & 60 lpcd. Rural Habitations .. 20 to 40 lpcd. |
| 7. | Water requirement per day | : | Base year supply (2006) .. 68 Million litres per day Ultimate supply (2036) .. 100 Million litres per day |
| 8. | Beneficiaries under this scheme | : | Municipalities .. 5 Nos Town Panchayats .. 11 Nos. Rural Habitations .. 3163 Nos. in 18 Panchayat unions of Pudukkottai, Sivagangai and Ramnad Districts. |

9.BENEFICIARIES

a. Pudukottai District.

i. Town Panchayat 			: Ponnamaravathy UTP.

ii. Rural Habitations			: 32Nos.

b. Sivagangai District.

i. Municipalities			: Sivagangai Municipality.

ii. Town Panchayats			: Thiruppathur

Nerkuppai

Ilayankudi

iii. Rural Habitations			: 799Nos

c. Ramanathapuram District.

i. Municipalities 			: Ramanathapuram

Paramakudi

Keelakarai

Rameswaram

ii. Town Panchayats 			: Thondi

R.S.Mangalam

Mandapam

Mudukulathur

Abiramam

Kamuthi

Sayalkudi

iii. Rural Habitations 		: 2332Nos.

10. COST				: Total Expenditure as per Execution –

Rs.671.592Crores.

HEAD WORKS

|  | Collector well I | Collector well II | Collector well III | Collector well IV |
| --- | --- | --- | --- | --- |
| Dia of well | 6.00m | 6.00m | 6.00m | 6.00m |
| Depth of well | 17.50m | 18.05m | 15.75m | 17.50m |
| Length of Foot Bridge | 678m | 715m | 485m | 178m |
| Connecting main size and length. | 700mm dia 690 m | 600mm dia 1150 m | 600 mm dia 1780 m | 600mm dia 3960 m |
| Duty of Vertical Turbine Hollow shaft pumpsets | 16870 lpm x 22.56m – H, 120HP | 16870 lpm x 24.56m – H, 125HP | 16870 lpm x 25.56m - H, 150HP | 16870 lpm x 29.56m-H, 150HP |

| Component | Numbers | Inner dia | Storage depth | Duty of pumpsets |
| --- | --- | --- | --- | --- |
| 20 LL Sumps | 2 Nos. | 29.80 m | 2.75 m | -- |
| 5 LL Sump cum Pumphouse. | 2 Nos. | 10.00 m | 6.35 m | 3 x 2 Nos. Vertical Turbine Solid shaft pumpset 16870 lpm x 91.5 m - H |

Booster Station at Poruvai

| 20 LL Sumps | 2 Nos. | 25.25 m | 4.00 m | -- |
| --- | --- | --- | --- | --- |
| 5 LL Sump cum Pumphouse. | 2 Nos. | 10.00 m | 4.81 m | 3 x 2 Nos. Vertical Turbine Solid shaft pumpset 16790 lpm x 84 m - H |

PACKAGE I

| 1 | ### Pumpsets at Booster station | 1.5 HP submersible – 2 Nos. (100% stand bye) 153 lpm x 19m head 7.5 HP submersible - 2 Nos. (100% stand bye) 234 lpm 47 m head |
| --- | --- | --- |
| 2 | ### Pumping Main | Mutharasanallur to Poruvai sump 1220 mm ms pipes- 34.60 km |
| 3 | Feeder main for Rural habitations PVC | 140mm PVC 6ksc Pipe 1617M 110 mm PVC 6ksc Pipe 1463 M 90 mm PVC 6ksc Pipe 5901 M 90 mm PVC 4ksc Pipe 7351 M 75 mm PVC 6ksc Pipe 11180 M 63 mm PVC 6ksc Pipe 958 M 63 mm PVC 4ksc Pipe 19369 M Total - 47893 M |

PACKAGE II

| 1 | ### Pumpsets at Booster station |  |  | 428 HP Turbine –6Nos(50% Stand bye)16790 lpmx84M |  |
| --- | --- | --- | --- | --- | --- |
| 2 | ### Pumping Main |  |  | Poruvai To ALAVAYAL sump 1220 mm ms pipes-45.655 km |  |
| 3 | ##### Feeder main to Ponnamaravathy T.P |  |  | 200 mm PVC Pipe 891.90 M 140 mm PVC Pipe 1381.10 M |  |
| 4 | Feeder main for Rural habitations PVC |  |  | 200 mm PVC 4ksc Pipe 7297.10 M 160 mm PVC 4ksc Pipe 8434.50 M 160 mm PVC 6ksc Pipe 13862.80 M 110 mm PVC 6ksc Pipe 2126.60M 63 mm PVC 4ksc Pipe 926.70 M 50 mm PVC 6ksc Pipe 3467.65M |  |
|  | ##### HDPE Pipes |  | 160 mm HDPE PN 8 Pipe 5704.50 M 140 mm HDPE PN 8 Pipe 737.20 M 110 mm HDPE PN 8 Pipe 6696.70M 63 mm HDPE PN 8 Pipe 81.85 M 50 mm HDPE PN 8 Pipe 2518.90M |  |  |
| 5 | Group sumps and pumpsets |  |  |  |  |
| Sl.No | Location | Sump Cap |  |  | Pumpset Details |
| 1 | At Poruvai |  |  |  |  |
|  | a) | 5.00 LL |  |  | Vertical Turbine 428 HP x 3 Nos. |
|  | b) | 5.00 LL |  |  | Vertical Turbine 428 HP x 3 Nos. |
| 2 | At Alavayal |  |  |  |  |
|  | a) | 25.00LL |  |  |  |
|  | b) | 25.00LL |  |  |  |
|  | c) | 25.00LL |  |  |  |
| 3 | At Ponnamaravathy |  |  |  |  |
|  | a) | 0.60 LL |  |  | Horizontal split casing 12.5.HP x 2 |
|  |  | Covered under Pkg.III |  |  |  |
| 4 | At Mavoor |  |  |  |  |
|  | a) | 0.10 LL |  |  | Open well Submersible 2 HP x 2 |

PACKAGE III

| 1 | ### Gravity Main | Alavayal Sump to Kalayarkoil MSR 1100mm PSC Main-60.329KM 1100mm BWSC Main-9.299KM |
| --- | --- | --- |
| 2 | ### Benefitted Town Panchayat | NERKUPPAI TOWN PANCHAYAT Sump Capacity-0.30LL Pump room Size-3x3m Pumpset-4HP Submersible Pumpset-2 nos Feeder main Length 110mm PVC Pipe-294m 90mm PVC Pipe-164m 63mm PVC Pipe-16722m No of S.R newly Constructed 30000 Litre -1no 10000 Litre-4nos Distribution Syatem Laid 63mm PVC Pipe-2228 Public Fountain-11 Nos THIRUPPATHURTOWN PANCHAYAT Sump Capacity-1.00LL Pump room Size-5x4m Pumpset-20HP HSC Pumpset-2 nos Feeder main Length 250mm HDPE PVC Pipe - 4390m 90mm PVC Pipe - 600M |
| 3 | ##### Benefitted Union | KALLAL UNION No of Main Sump-2 nos 1 at Aranmanai Siruvayal 2 at Pattamangalam Main Sump at Aranmanai Siruvayal Capacity of Sump:3.00 LL No of Feeder Main -2 nos No of Pumping Main -3 nos Pump room Size-8mx5m Pumpset- Summersible Pump set 5x2 nos No of Intermediate Sump :3 Nos 1 ) At Panangudi Capacity of Sump:1.00 LL No of Feeder Main -1 nos Pump room Size-3mx3m Pumpset- Summersible Pump set 1x2 nos 2 ) At Vertriyur Capacity of Sump:1.00 LL No of Feeder Main -1 nos Pump room Size-3mx3m Pumpset- Summersible Pump set 1x2 nos 3) At Anna Nagar Capacity of Sump:1.00 LL No of Feeder Main -1 nos Pump room Size-3mx3m Pumpset- Summersible Pump set 1x2 nos Main Sump at Pattamangalam Capacity of Sump:3.00 LL No of Feeder Main -2 nos No of Pumping Main -2 nos Pump room Size-5mx4m Pumpset- Summersible Pump set 4x2 nos No of Intermediate Sump :2 Nos 1) At Pillaiyarpatty Capacity of Sump:2.00 LL No of Feeder Main -3 nos Pump room Size-5mx4m Pumpset- Summersible Pump set 3x2nos 1 A) At Arcot Capacity of sump : 0.10 LL Pump room : Kiosk 2 ) At North Avanthipatty Capacity of Sump:2.00 LL No of Feeder Main -2 nos No of Pumping Main -1no Pump room Size-3mx3m Pumpset- Summersible Pump set 3x2nos 2a) At Vadugapatti Capacity of sump : 0.05 LL Pump room : Kiosk 2b) At Melamahanam Capacity of Sump:3.00 LL No of Feeder Main -1 nos Pump room Size-3mx3m Pumpset- Summersible Pump set 1x2 nos 2c) At Thalakkavoour ADC Capacity of sump : 0.10 LL Pump room : Kiosk No Of New S.R Constructed 30000 Litre -2nos 10000 Litre-12nos 5000 Litre GLSR-4 Nos Distribution Syatem Laid 63mm PVC Pipe-4850m Public Fountain-40 Nos |
| 4 | Feeder main for Rural habitations and Pumping mains From Sump to Sump | 160 mm PVC 6ksc Pipe 12230 M 140 mm PVC 6ksc Pipe 2200 M 140 mm PVC 4ksc Pipe 15580 M 110 mm PVC 4ksc Pipe 41310M 90 mm PVC 4ksc Pipe 32570 M 75mm PVC 4ksc Pipe 20020M 63mm PVC 4ksc Pipe 64975M 75mm PVC 4ksc Pipe 79775M |
| 5 | Kalayarkoil MSR | Capacity :10.00 LL Staging Height :14m |

PACKAGE IV

| 1 | Gravity Main & Branch Gravity Main. | MSR at Kallal - 2.00 Lakh Lit-1No. 600mm to 350mm PSC pipe - 87.47KM 300mm to 100mm CI pipe - 46.67KM |
| --- | --- | --- |
| 2 | Benefitted Town Panchayat | THONDI TOWN PANCHAYAT Sump Capacity-0.60LL Pump room Size-5x4m Pumpset-10HP HSC Pumpset-2 nos Feeder main Length 160mm PVC Pipe - 18M 110mm PVC Pipe - 916M 75mm PVC Pipe - 2864M R.S.MANGALAM TOWN PANCHAYAT Sump Capacity-0.60LL Pump room Size-8x5m Pumpset-7.5HP HSC Pumpset-2 nos Feeder main Length 160mm PVC Pipe - 2184M 140mm PVC Pipe - 160M 90mm PVC Pipe - 1365M |
| 3 | ##### Benefitted Union | DEVAKOTTAI UNION No of Main Sump-2 nos 1 at Muppaiyur vilakku 2 at Pagayani Main Sump at Muppaiyur vilakku Capacity of Sump:2.00 LL Pump room Size-8mx5m Pumpset- Summersible Pump set 5x2 nos Main Sump at Pagayani Capacity of Sump:1.50 LL Pump room Size-8mx5m Pumpset- Summersible Pump set 4x2 nos Feeder main to rural habitations 140mm PVC 4 KSC Pipe – 4675m 110mm PVC 4 KSC Pipe – 6751m 110mm PVC 6 KSC Pipe – 23365m 90mm PVC 4 KSC Pipe – 53241m 75mm PVC 4 KSC Pipe – 23771m 63mm PVC 4 KSC Pipe – 51854m 50mm PVC 6 KSC Pipe – 60626m THIRUVADANAI UNION No of Main Sump - 5 nos 1 at Orikottai 2 at Kadambur 3 at Kattivayal 4 at Pandugudi 5 at Kulathur Main Sump at Orikottai Capacity of Sump:2.00 LL Pump room Size-8mx5m Pumpset- Submersible Pump set 5x2 nos Main Sump at Kadambur Capacity of Sump:3.00 LL Pump room Size-5mx4m Pumpset- Submersible Pump set 5x2 nos Main Sump at Kattivayal Capacity of Sump:3.00 LL Pump room Size-5mx4m Pumpset- Submersible Pump set 4x2 nos Main Sump at Pandugudi Capacity of Sump:1.50 LL Pump room Size-5mx4m Pumpset- Submersible Pump set 5x2 nos Main Sump at Kulathur Capacity of Sump:2.00 LL Pump room Size-5mx4m Pumpset- Submersible Pump set 3x2 nos Feeder main to rural habitations 160mm PVC 4 KSC Pipe – 11269m 140mm PVC 4 KSC Pipe – 8068m 110mm PVC 4 KSC Pipe – 27228m 90mm PVC 4 KSC Pipe – 51774m 75mm PVC 4 KSC Pipe – 41080m 63mm PVC 4 KSC Pipe – 160882m 50mm PVC 6 KSC Pipe – 145971m R.S.MANGALAM UNION No of Main Sump - 5 nos 1 at Anandur Vilakku 2 at A.R.Mangalam 3 at Union Office 4 at Thiruppalaikudi Vilakku 5 at Periyakanmoi Main Sump at Anandur Vilakku Capacity of Sump:3.00 LL Pump room Size-5mx4m Pumpset- Submersible Pump set 4x2 nos Main Sump at A.R.Mangalam Capacity of Sump:3.00 LL Pump room Size-5mx4m Pumpset- Submersible Pump set 4x2 nos Main Sump at Union Office Capacity of Sump:2.00 LL Pump room Size-5mx4m Pumpset- Submersible Pump set 4x2 nos Main Sump at at Thiruppalaikudi Vilakku Capacity of Sump:2.00 LL Pump room Size-5mx4m Pumpset- Submersible Pump set 3x2 nos Main Sump at Periyakanmoi Capacity of Sump:1.50 LL Pump room Size-5mx4m Pumpset- Submersible Pump set 3x2 nos Feeder main to rural habitations 160mm PVC 4 KSC Pipe – 4080m 140mm PVC 6 KSC Pipe – 12330m 140mm PVC 4 KSC Pipe – 20556m 110mm PVC 4 KSC Pipe – 40185m 90mm PVC 4 KSC Pipe – 48484m 75mm PVC 4 KSC Pipe – 49127m 63mm PVC 6 KSC Pipe – 930m 63mm PVC 4 KSC Pipe – 137837m 50mm PVC 6 KSC Pipe – 117337m |
|  | ##### Sumps | 38Nos Urban sump -2Nos,(Thondi & R.S.Mangalam) Main rural sump – 15Nos. Regrouping sump – 21Nos. |
|  | Distribution system | 34.00KM. |

PACKAGE V

| 1 | ### Gravity Main | Alavayal Sump to Kalayarkoil MSR 1200mm PSC Main -2.610KM 1000mm PSC Main-28.994 KM |
| --- | --- | --- |
| 2 | ### Pumping Main | From Kalayarkoil Sivagangai Municipality 350 mm PSC – 12 KSC pipe - 10170 m 350 mm PSC – 10 KSC pipe - 2100 m 350 mm PSC – 8 KSC pipe - 2913 m 350 mm PSC – 6 KSC pipe - 780 m 350 mm PSC – 4 KSC pipe - 3707 m Total - 19670 m |
| 3 | ### Benefited Municipality | Sivagangai Municipality Sump Capacity-3.00LL Pump room Size-8x5m Pumpset-50HP HSC Pumpset-2 nos Feeder main Length to existing & new service reservoirs 315 mm HDPE Pipe – PN 6 class- 441 M 200 mm PVC 4 KSC – 81 m 140 mm PVC 4 KSC - 20 m 110 mm PVC 4 KSC - 950 m ----------- Total - 1492 m S.R newly Constructed - 4.00 lakh Litre -1no |
| 4 | ### Benefited Town panchayat | ILAYANKUDI TOWN PANCHAYAT Sump Capacity-1.00 LL Pump room Size-5x4m Pumpset- 7.5HP HSC Pumpset- 2 nos Feeder main Length 200 mm PVC 4 KSC – 168 m 110 mm PVC 4 KSC - 800 m 75mm PVC 4 KSC - 1030 m 63 mm PVC 4 KSC - 4013 m 50 mm PVC 6 KSC - 538 m Total - 6549 m ------------ |
| 5 | ##### Benefited Union | KALAYARKOIL UNION No of Main Sump-3 nos 1 at Kalayarkoil 2 at Paruthikanmoi and at Ilanthakarai Main Sump at Kalayarkoil Capacity of Sump:1.00 LL Pump room Size- 11 x 8.7m Pumpset- Horizontal split casing centrifugal pumpset – 3192 lpm X 48 m Head - 50 HP x 2 Nos. Submersible Pump set 3X2 nos No of Intermediate Sump :2 Nos 1 ) At Kollangudi Capacity of Sump:1.00 LL Pump room Size-3x3m Pumpset- Submersible Pump set 3x2 nos 1a) At Kandipatti Capacity of sump : 0.05 LL Pump room : Kiosk Pumpset- Submersible Pump set 1x2 nos 2 ) At Thiruvelangudi Capacity of Sump:1.00 LL Pump room Size-3x3m Pumpset- Submersible Pump set 1x2 nos 2a) At Chinnaponnampatti Capacity of sump : 0.05 LL Pump room : Kiosk Pumpset- Submersible Pump set 1x2 nos 2b) At Chockkanathpuram Capacity of sump : 0.05 LL Pump room : Kiosk Pumpset- Submersible Pump set 1x2 nos Main Sump at Paruthikanmoi Capacity of Sump: 2.00 LL Pump room Size-8x5m Pumpset- Submersible Pump set 5x2 nos No of Intermediate Sump :4 Nos 1 At Maravamangalam Capacity of Sump:1.00 LL Pump room Size-3x3m Pumpset- Submersible Pump set 3x2 nos 2 ) At Uruvatti Capacity of Sump: 1.00 LL Pump room Size-3x3m Pumpset- Submersible Pump set 2x2nos 3) At Periyakannanur Capacity of Sump:2.00 LL Pump room Size-3x3m Pumpset- Submersible Pump set 1x2 nos 4) At Satharasankottai Capacity of Sump:1.00 LL Pump room Size-3x3m Pumpset- Submersible Pump set 3x2 nos Main sump at Ilanthakarai Capacity of Sump: 1.50 LL Pump room Size-8x5m Pumpset- Submersible Pump set 4x2 nos No of Intermediate Sump :1 No 1) At Kundakudai Capacity of Sump:1.00 LL Pump room Size-3x3m Pumpset- Submersible Pump set 1x2 nos No Of New S.R Constructed 10000 Litre-5 nos 5000 Litre GLSR-5 Nos Distribution System Laid 63mm PVC Pipe-1410m Public Fountain-8 Nos |
| 6 | Feeder main for Rural habitations and Pumping mains From Sump to Sump in Kalayarkoil Union | 140 mm PVC4ksc Pipe 15560 M 110 mm PVC 6ksc Pipe 3167 M 110 mm PVC 4ksc Pipe 84920 M 90 mm PVC 4ksc Pipe 31180 M 75 mm PVC 4ksc Pipe 41373 M 63 mm PVC 6ksc Pipe 1890 M 63 mm PVC 4ksc Pipe 93231 M 50 mm PVC 6ksc Pipe 145748 M ----------- TOTAL 417069 M --------------- |
| 7 | ##### Benefited Union | ILAYANKUDI UNION No of Main Sump-3 nos 1 at Kannamangalam 2 at Kalankathankottai and at Gaberiyalpattinam Main Sump at Kannamangalam Capacity of Sump:1.50 LL Pump room Size- 5 x 4 m Submersible Pump set 3X2 nos No of Intermediate Sump :2 Nos 1 ) At Ariyamangalam Capacity of Sump:1.00 LL Pump room Size-3x3m Pumpset- Submersible Pump set 1x2 nos 1a) At Enthal Capacity of sump : 0.05 LL Pump room : Kiosk Pumpset- Submersible Pump set 1x2 nos 2 ) At Kodimangalam Capacity of Sump:1.00 LL Pump room Size-3x3m Pumpset- Submersible Pump set 2x2 nos 2a) At Alambacheri Capacity of sump : 0.05 LL Pump room : Kiosk Pumpset- Submersible Pump set 1x2 nos Main Sump at Kalankathankottai Capacity of Sump: 2.00 LL Pump room Size-5x4 m Pumpset- Submersible Pump set 3x2 nos No of Intermediate Sump :3 Nos 1 At Virayathakandan Capacity of Sump:2.00 LL Pump room Size-3x3m Pumpset- Submersible Pump set 3x2 nos 2 ) At Utchani Capacity of Sump: 1.00 LL Pump room Size-3x3m Pumpset- Submersible Pump set 2x2nos 3) At Seevalathi Capacity of Sump: 2.00 LL Pump room Size-3x3m Pumpset- Submersible Pump set 3x2 nos 3a) At Varunthi Capacity of sump : 0.05 LL Pump room : Kiosk Pumpset- Submersible Pump set 1x2 nos Main sump at Gaberiyalpattinam Capacity of Sump: 2.00 LL Pump room Size-5x4m Pumpset- Submersible Pump set 3x2 nos No of Intermediate Sump :2 Nos 1) At Athikarai Capacity of Sump:2.00 LL Pump room Size-3x3m Pumpset- Submersible Pump set 2x2 nos 2) At Vani Capacity of Sump:1.50 LL Pump room Size-3x3m Pumpset- Submersible Pump set 2x2 nos 2a) At Kalvelipottal Capacity of sump : 0.05 LL Pump room : Kiosk Pumpset- Submersible Pump set 1x2 nos No Of New S.R Constructed 30000 litre – 3 Nos 10000 Litre-3 nos 5000 Litre GLSR-3 Nos Distribution System Laid 63mm PVC Pipe-4150 m Public Fountain-18 Nos |

PACKAGE VI

| 1 | ###### Gravity Main from R.S Mangalam Cross to Pamban Sump – Package VI |  |
| --- | --- | --- |
| a) | Transmision main |  |
|  | Gravity PSC | 800 - 500 mm dia PSC Pipe- 78435 M |
|  | ## Pumping Main | 400 mm dia PSC Pipes – 8800 M |
|  |  | HDPE 200 mm dia PN.6 Pipes - 7335 M |
|  |  | PVC 200 mm dia PSC Pipes - 10065 M |
| b) | Branch Main From Transmission Main to Sump |  |
|  |  | PSC 500 –350 mm & CI 150 mm – 300 - 88610 M |
|  |  | Total - 193245 M |
| c) | Feeder main & Branch Feeder Main |  |
|  |  | PSC Pipe 350-mm - 1565 M |
|  |  | CI Pipe 15 M |
|  |  | HDPE 280-MM, 250-M & 160-MM Pipe – 5960 M |
|  |  | PVC 250 mm – 50 mm Pipe 1054428 M |
|  |  | CI 150-40 mm Pipes 3040 M |
|  |  | Total -1065008 M |
| 2 | Sumps for Beneficieries | Total – 27 Nos |
|  |  | 20.00 Lakhs Litres capacity - 1 No |
|  |  | 5.00 Lakhs Litres Capacity - 1No. |
|  |  | 4.00 Lakhs Litres Capacity - 5 Nos |
|  |  | 3.00 Lakhs Litres Capacity - 9 Nos |
|  |  | 2.00 Lakhs Litres Capacity - 4 Nos |
|  |  | 1.50 Lakhs Litres Capacity - 3 No.s |
|  |  | 1.00 Lakhs Litres capacity - 3 Nos |
|  |  | 0.60 Lakhs Litres Capacity - 1 No. |
|  |  | Total – 27 Nos |
| 3 | Service Reservoirs - 204 Nos |  |
|  |  | Total – 27 Nos |
|  |  | 5.00 Lakhs Litres Capacity - 3Nos. |
|  |  | 2.00 Lakhs Litres Capacity - 1 No |
|  |  | 1.00 Lakhs Litres Capacity - 1 No |
|  |  | 0.60 Lakhs Litres Capacity - 1 No |
|  |  | 0.30 Lakhs Litres Capacity - 34 Nos |
|  |  | 0.10 Lakhs Litres Capacity - 99 Nos |
|  |  | 0.05 Lakhs Litres Capacity -65 Nos |
|  |  | Total – 204 Nos |
| 4 | Pump Rooms | 11 x 8.7 m size - 1 No |
|  |  | 8 x 5.0 m Size - 2 Nos |
|  |  | 5 x 4.0 m Size - 22 Nos |
|  |  | 2 x 2.0 m Size (Existing) - 1 No |
|  |  | Total 26 Nos |
| 5 | Distribution System | 75.923 Km |

PACKAGE VII

| Sl. No. | Name of component | Total quantity in KM |
| --- | --- | --- |
| 1a) | Transmission main (Gravity) - PSC 900mm to 350mm |  |
|  | 900 mm - 10 ksc | 9.070 |
|  | 800 mm - 12 ksc | 0.915 |
|  | 800 mm - 10 ksc | 15.056 |
|  | 700 mm - 12 ksc | 11.411 |
|  | 600mm - 14 ksc | 5.937 |
|  | 600mm - 12 ksc | 0.350 |
|  | 500mm - 16 ksc | 0.830 |
|  | 500mm - 14 ksc | 12.713 |
|  | 350mm - 16 ksc | 5.535 |
| b)(i) | Br Gravity main - PSC 350mm |  |
|  | 500mm - 12 ksc | 4.434 |
|  | 350mm - 16 ksc | 9.710 |
|  | 350mm - 14 ksc | 13.530 |
|  | 350mm - 10 ksc | 0.080 |
| (ii) | Br Gravity Main-CI 300 to 125mm | 34.180 |
| c)(i) | Br Conveying main(Pumping) PSC 500mm to 350mm |  |
|  | 450mm - 10 ksc | 4.655 |
|  | 450mm - 8 ksc | 8.550 |
|  | 450mm - 6 ksc | 1.135 |
|  | 350mm - 6 ksc | 19.435 |
|  | 350mm - 4 ksc | 2.544 |
| (ii) | Br Conveying main(Pumping)CI 300mm to 125mm | 52.003 |
|  | Total | 212.073 |
| 2a | Feeder main & Br.Feeder main PSC 350mm |  |
|  | 350mm - 8 ksc | 1.685 |
|  | 350mm - 6 ksc | 1.545 |
| 2b | Feeder main & Br.Feeder main HDPE 315mm to 250mm, | 2.180 |
| 2c | Feeder main & Br.Feeder main PVC 250mm to 50mm | 1248.363 |
| 2d | Feeder main & Br.Feeder main GI 150mm to 40mm | 14.151 |
| 2e | Feeder main & Br.Feeder main CI 300mm | 0.030 |
|  | Total | 1267.954 |
| 3 | Sump --31 Nos |  |
|  | 8.00 Lakh .Litre | 1 No |
|  | 1.50 Lakh Litre | 1 No |
|  | 5.00 Lakh Litre | 1 No |
|  | 4.00 Lakh Litre | 7 No |
|  | 3.00 Lakh Litre | 7 No |
|  | 2.00 Lakh Litre | 6 No |
|  | 7.00 Lakh Litre | 1 No |
|  | 1.00 Lakh Litre | 2 No |
|  | 0.60 Lakh Litre | 3 No |
|  | 0.30 Lakh Litre | 2 No |
| 4 | Pump sets | 126 No |
| 5 | Service Reservoir (165 Nos) |  |
|  | GLSR | 66 No |
|  | 10000 | 63 No |
|  | 30000 | 30 No |
|  | 60000 | 5 No |
|  | 100000 | 1 No |
| 6 | Pump rooms (27Nos) |  |
|  | 11 M x 8.7M | 1 No |
|  | 8 M x 5 M | 16 No |
|  | 5 M x 4 M | 10 No |
| 7 | Distribution system | 72.100 km |