## folder
TAMIL NADU WATER SUPPLY AND DRAINAGE BOARD
OFFICE OF THE CHIEF ENGINEER,
OPPOSITE TO MATTUTHAVANI BUS STAND,
1/1, SAMBAKULAM, MADURAI -625007
Operation and maintenance of the CWSS to 239 Costal habitations in Thoothukudi District, Virudhunagar, Aruppukottai Municipalities, Kariyapatti & Mallankinaru Town Panchayats including CWSS To 67 Rural Habitations in Virudhunagar District including repair and rectification works for the period From 16.07.2022 To 31.03.2023
BILL OF QUANTITES

## BillofQty
NAME OF SCHEME :- Operation and maintenance of the CWSS to 239 Costal habitations in Thoothukudi District, Virudhunagar, Aruppukottai Municipalities, Kariyapatti & Mallankinaru Town Panchayats including CWSS To 67 Rural Habitations in Virudhunagar District including repair and rectification works for the period From 16.07.2022 To 31.03.2023
BILL OF QUANTITIES
General
The Bill of Quantities shall contain items for the construction, installation, testing, commissioning and maintenance of the Works to be carried out by the Contractor
The Bill of Quantities will be used to calculate the Contract Price. The contractor shall be paid for the quantum of work done at the rate furnished for each item in the Bill of Quantities.
Where there is a discrepancy between the rates in words and figures, the lesser of the two will only be taken into consideration.
Where there is a discrepancy between the unit rate and line item total resulting from multiplying the unit rate by the quantity, the unit rate as quoted will govern.
Where there is an arithmetical discrepancy in the page total as well as grand total, the corrected total by the Employer will govern
The rates furnished in the BOQ shall be for carrying out the work in conformity to the BIS, TNBP and Technical Specifications and other Terms and Conditions set out in the Bid Document
All pages in the BOQ should be signed without omission. All corrections/over writing should be properly attested by the Bidder.
Change in the Quantities
If the final quantity of the work done differs from the quantity in the Bill of Quantities for the particular item/items, the rates as in the agreement for the relevant items shall be paid.
GST
GST is applicable as per GO. 296, Finance(salaries) Dept. Dt. 09.10.2017, GOI, Ministry of finance – central tax (Rate) New Delhi, notification No. 11/2017/ Dt. 28.06.2017 and as amended from time to time.From every payment made to the firm/ contractor, deduction at source towards GST shall be made for civil works contract as per Government of India, Ministry of Finance/ Department of Revenue, New Delhi Notification No. 20 / 2017 – Central Tax (Rate) / Dt.22.08.2017 subject to issue of amendments from time to time.
Name of Work :
Operation and maintenance of the CWSS to 239 Costal habitations in Thoothukudi District, Virudhunagar, Aruppukottai Municipalities, Kariyapatti & Mallankinaru Town Panchayats including CWSS To 67 Rural Habitations in Virudhunagar District including repair and rectification works for the period From 16.07.2022 To 31.03.2023
-----------------------------------------------------------------------------------------------------------------
Sl.No. Description of Quantity Specifi Unit Rate Amount
Item of Work cation ---------------------------
in in
Figures Words
-----------------------------------------------------------------------------------------------------------------

## General Abstract
General Abstract
NAME OF WORK : Operation and maintenance of the CWSS to 239 Costal habitations in Thoothukudi District, Virudhunagar, Aruppukottai Municipalities, Kariyapatti & Mallankinaru Town Panchayats including CWSS To 67 Rural Habitations in Virudhunagar District including repair and rectification works for the period From 16.07.2022 To 31.03.2023
Schedule | Description | Amount in Rs.
OPERATION AND MAINTENANCE OF THE FOLLOWING CWSS TO SUPPLY EARMARKED QUANTITY OF WATER NOTED AGAINST EACH CWSS IN THIRUNELVELI DISTRICT BY CARRYING OUT ALL THE NECESSARY WORKS SUCH AS PUMPING, ATTENDING TO LEAK AND BURST, ATTENDING TO ELECTRICAL AND MECHANICAL REPAIR WORKS, PROVIDING DISINFECTION, PREVENTIVE MAINTENANCE OF ALL INSTALLATIONS, SUMP CLEANING AND DELIVERANCE OF EARMARKED QUANTITY OF WATER TO THE BENEFICIARIES AS PER SCHEDULE AND STANDARD OPERATING PROCEDURES AND AS DIRECTED BY THE TWAD BOARD OFFICERS FOR A PERIOD UPTO 31.03.2023
A1 | CWSS to 239 Costal habitations in Thoothukudi District, Virudhunagar, Aruppukottai Municipalities, Kariyapatti & Mallankinaru Town Panchayats including CWSS To 67 Rural Habitations in Virudhunagar District including repair and rectification works for the period From 16.07.2022 To 31.03.2023 | 0
| TOTAL | 0

## 239
Schedule - A1
Name of Scheme: Operation and maintenance of the CWSS to 239 Costal habitations in Thoothukudi District, Virudhunagar, Aruppukottai Municipalities, Kariyapatti & Mallankinaru Town Panchayats including CWSS To 67 Rural Habitations in Virudhunagar District including repair and rectification works for the period From 16.07.2022 To 31.03.2023
Sl.No | Description of work | Quantity |  | TNBP No. Other specification | Unit | Rate |  | Amount in Rs.
[6 empty] | in figures | in words
1 | Operation and Maintenance of the Electro Mechanical installations, equipments, components, pipelines valves and appurtenances, water retaining structures including protecton of all schemee components from damages/ theft undertaking legal actions for such untoward incidents, preventive maintenance, disinfection and deliverance of water as per quality standards and supply of earmarked quantity of water 14.00 MLD to the beneficiaries as per Annexure carrying out the O&M as per standard operating procedures, Acts and rules in force etc., complete and as directed by TWAD Board Oficers and excluding cost towards attending leak, burst repair and replacement works to electro mechanical installations consumables for disinfection of water, cleaning of all water retaining structure, electricity - Totally 3626.000 ML (14 MLD x 259) | 3626 | ML | Special Specification | One ML
2) | Attending collar Leaks occurred in all the size, class and material of pipes in all the pipelines of this CWSS for the following items round the clock as per the standard specifications including earthwork excavation ,removal of slushy soil , labour charges, civil works, cost of materials, dewatering , genset, welding unit,and providing night lamps, barrigading arrangements, caution sign boards ,trafic diversion arrangements and all other incidental charges, etc complete within the stipulated time limit as specified in Clause 2.2.5 of General conditions of Contract Part II.and as directed by TWAD Board officers
i) | Earth work excavation and depositing on bank in hard stiff clay, stiff black cotton soil, hard red earth, shales, murrams, ordinary gravel stoney earth mixed with small sized boulders etc., for leak rectification works for the following sizes of Pipes and as directed by TWAD Bd. Officers |  |  | SS 20 B,23, 95 and Special specifications
a) | For AC Pipes of various classes | 30.022 | m3 |  | One Cubic metre
b) | For PSC Pipes of various classes | 585.115 | m3 |  | One Cubic metre
ii) | Supply and delivery of lead wool as per sample including loading, unloading and transportation charges etc. complete and as directed by TWAD Bd. Officers |  |  | Special Specification
a) | 250 mm AC of Various Classes | 32 | Kg |  | One Kg
b) | 350 mm PSC of Various Classes | 20 | Kg |  | One Kg
c) | 500 mm PSC of Various Classes | 85 | Kg |  | One Kg
d) | 600 mm PSC of Various Classes | 180 | Kg |  | One Kg
iii) | Supply and delivery of Hard crete oil including loading, unloading and transportation charges etc. complete and as directed by TWAD Bd. Officers |  |  | Special Specification
a) | 250 mm AC of Various Classes | 40 | lit |  | One litre
b) | 350 mm PSC of Various Classes | 20 | lit |  | One litre
c) | 500 mm PSC of Various Classes | 85 | lit |  | One litre
d) | 600 mm PSC of Various Classes | 180 | lit |  | One litre
iv) | Supply and delivery of cement including loading, unloading and transportation charges etc. complete and as directed by TWAD Bd. Officers |  |  | SS 10 and Special Specification
a) | 250 mm AC of Various Classes | 48 | Kg |  | One Kg
b) | 350 mm PSC of Various Classes | 30 | Kg |  | One Kg
c) | 500 mm PSC of Various Classes | 119 | Kg |  | One Kg
d) | 600 mm PSC of Various Classes | 252 | Kg |  | One Kg
v) | Dewatering using 5HP diesel engine pumpset including Hire charges, cost of Diesel, Engine oil, pump operator, labour charges, conveyance of pumpset and fuel to site and back, loading, unloading and any other incidental charges etc., complete and as directed by TWAD Bd. Officers |  |  | Special Specification
a) | 250 mm AC of Various Classes | 32 | Hours |  | One Hour
b) | 350 mm PSC of Various Classes | 20 | Hour |  | One Hour
c) | 500 mm PSC of Various Classes | 85 | Hour |  | One Hour
d) | 600 mm PSC of Various Classes | 216 | Hour |  | One Hour
iii) | Supply and delivery of the following sizes of following pipes confirming to IS and other specifications including transportation charges any where in Tamilnadu etc., complete and as direced by the TWAD Board Officers. |  |  | IS 1592 / 2003 and as amended from time to time and special specification
a | 250mm AC class 15 pipe | 8 | m |  | One metre
vi) | Refilling with excavated soil (other than sand)complying with standard specification in layers of 15cm watered well rammed and consolidated after the pipes and specials are laid,jointed and tested etc. and removing and depositing the surplus earth at the place shown by the TWAD Board Officers |  |  | SS 24, 95 and Special specifications
a | For AC Pipes of various classes | 30.022 | m3 |  | One Cubic metre
a | For PSC Pipes of various classes | 585.115 | m3 |  | One Cubic metre
2) b | Attending Leaks occurred in all the size, class and material of pipes in all the pipelines of this CWSS for the following items with SS Clampsets round the clock as per the standard specifications including earthwork excavation, removal of slushy soi, labour charges, civil works, cost of materials, dewatering , and providing night lamps, barrigading arrangements, caution sign boards ,trafic diversion arrangements and all other incidental charges, etc complete within the stipulated time limit as specified in Clause 2.2.5 of General conditions of Contract Part II.and as directed by TWAD Board officers.
i) | Earth work excavation and depositing on bank in hard stiff clay, stiff black cotton soil, hard red earth, shales, murrams, ordinary gravel stoney earth mixed with small sized boulders etc., for leak rectification works for the following sizes of Pipes and as directed by TWAD Bd. Officers |  |  | SS 20 B,23, 95 and Special specifications
a) | For PSC Pipes of various classes | 225.464 | m3 |  | One cubic metre
b) | For AC Pipes of various classes | 71.74 | m3 |  | One cubic metre
ii) | Supply and delivery of Leak Arresting Flexible MS Clamps of Suitable width of the clamps to be decided by the engineer incharge at site depending on the nature of pipe crack. |  |  | Special specifications
a) | 350mm MS clamp for PSC Pipe | 3 | No |  | Each
b) | 500mm MS clamp for PSC Pipe | 1 | No |  | Each
c) | 600mm MS clamp for PSC Pipe | 18 | No |  | Each
d) | For 250mm AC class 15 pipe | 16 | No |  | Each
iii) | Dewatering using 5HP diesel engine pumpset including Hire charges, cost of Diesel, Engine oil, pump operator, labour charges, conveyance of pumpset and fuel to site and back, loading, unloading and any other incidental charges etc., complete and as direced by the TWAD Board Officers. |  |  | Special Specification
a) | 350mm PSC Pipe | 12 | Hour |  | One Hour
b) | 500mm PSC Pipe | 5 | Hour |  | One Hour
c) | 600mm PSC Pipe | 108 | Hour |  | One Hour
d) | For 250mm AC class 15 pipe | 96 | Hour |  | One Hour
iv) | Refilling with excavated soil (other than sand)complying with standard specification in layers of 15cm watered well rammed and consolidated after the pipes and specials are laid,jointed and tested etc. and removing and depositing the surplus earth at the at the place shown by the TWAD Board Officers |  |  | SS 24, 95 and Special specifications
a) | For PSC Pipes of various classes | 225.464 | m3 |  | One Cubic metre
b) | For AC Pipes of various classes | 71.74 | m3 |  | One Cubic metre
3)a) | Attending burst occurred in all the size, class and material of pipes in all the pipelines of this CWSS for the following items with replacing the pipes round the clock as per the standard specifications including earthwork excavation ,removal of slushy soil , labour charges, civil works, cost of materials, dewatering , genset, welding unit,and providing night lamps, barrigading arrangements, caution sign boards ,trafic diversion arrangements and all other incidental charges, etc complete within the stipulated time limit as specified in Clause 2.2.5 of General conditions of Contract Part II.and as directed by TWAD Board officers
i) | Earth work excavation and depositing on bank in hard stiff clay, stiff black cotton soil, hard red earth, shales, murrams, ordinary gravel stoney earth mixed with small sized boulders etc., for leak rectification works for the following sizes of Pipes and as directed by TWAD Bd. Officers |  |  | SS 20 B,23, 95 and Special specifications
a | For PVC Pipes of various classes | 1484.053 | m3 |  | One Cubic metre
ii) | Removing following the burst Pipes from the pipe line and removal of slushy soil and baling out water and replacing the pipe line with sound pipe including jointing and cost of refilling the pipe line with water for retesting the pipe line etc complete (excluding cost of sound pipe and jointing materials and earth work) and as directed by the TWAD Board Officers |  |  | SS 20 B,23, 95 and Special specifications
a | 50mm PVC 6 KSC | 132 | nos. |  | Each
b | 63 mm PVC 6 KSC | 210 | nos. |  | Each
c | 75mm PVC 6 KSC | 84 | nos. |  | Each
d) | 90mm PVC 6 KSC | 72 | nos. |  | Each
e) | 110mm PVC 6 KSC | 18 | nos. |  | Each
e) | 140mm PVC 6 KSC | 58 | nos. |  | Each
e) | 160mm PVC 6 KSC | 20 | nos. |  | Each
iii) | Supply and delivery of the following sizes of PVC pipes confirming to IS and other specifications including transportation charges any where in Tamilnadu and as directed by the TWAD Board Officers |  |  | IS 4985/2000, and as amended from time to time and special specification
a | 50mm PVC 6 KSC | 132 | m |  | One metre
b | 63 mm PVC 4 KSC | 210 | m |  | One metre
c | 75mm PVC 4 KSC | 84 | m |  | One metre
d) | 90mm PVC 4 KSC | 72 | m |  | One metre
e) | 110mm PVC 4 KSC | 18 | m |  | One metre
e) | 140mm PVC 4 KSC | 58 | m |  | One metre
e) | 160mm PVC 4 KSC | 20 | m |  | One metre
iv) | Supply and delivery of following sizes of PVC Specials conforming to IS specifications inclusive of transportation charges anywhere in Tamilnadu and as directed by TWAD Board officers. |  |  | IS 10124/1982 Part - II, IS and amended from time to time and special specification
h | 50mm PVC Coupler Fabricated 6 KSC | 264 | Nos |  | Each
i | 63 mm PVC Coupler Fabricated 4 KSC | 420 | Nos |  | Each
h | 75mm PVC Coupler Fabricated 4 KSC | 168 | Nos |  | Each
i | 90mm PVC Coupler Fabricated 4 KSC | 144 | Nos |  | Each
h | 110mm PVC Coupler Fabricated 4 KSC | 36 | Nos |  | Each
h | 140mm PVC Coupler Fabricated 4 KSC | 116 | Nos |  | Each
h | 160mm PVC Coupler Fabricated 4 KSC | 40 | Nos |  | Each |  |  |  | 0
4) | Connection Main Pipe Leak work
i | Earthwork excavation below water level in light or sandy soil for infiltration gallery, syphon or connecting pipe line and connected works including shoring and strutting and charges for special tools and plants for bailing/ pumping etc., such asair compressor and helmet. |  |  | SS 20 B,23, 95 and Special specifications
a | 200mm DI K7 | 107.486 | m3 |  | One Cubic metre
ii | Suppluy and delivery of DI D/F Pipes onfirmation to IS inclusive of transportation charges anywhere in Tamil nadu etc complete and as directed by TWAD Board officers |  |  | AS PER IS 8329/2000
a | 200mm DI 2.5 m Length | 16 | Nos |  | Each
iii) | Lowering of D.I Pipes and specials in the trenches and laying to proper grade and alignment and as directed by the TWAD Officers |  |  | SS 97,98 and Special specifications
a | 200mm DI K7 | 80 | m |  | one metre
iv) | Jointing C.I/ D.I double flanged pipes and specials with rubber insertion or any equivalent to the required specifications with M.S. bolts and nuts etc., complete including charges for special tools and plants such as air compressor and helmets and sheet piles. etc for below water level(including cost of jointing materials) |  |  | SS 97,98 and Special specifications
a | 200mm DI K7 | 16 | Joint |  | Each Joint
5) | Attending Leak works in the Pumping main of 500mm MS Pipe
i) | Earth work excavation and depositing on bank in hard stiff clay, stiff black cotton soil, hard red earth, shales, murrams, ordinary gravel stoney earth mixed with small sized boulders etc., for leak rectification works for the following sizes of Pipes and as directed by TWAD Bd. Officers | 10.12 | m3 | SS 20 B,23, 95 and Special specifications | One Cubic metre
ii) | Dewatering using 5HP diesel engine pumpset including Hire charges, cost of Diesel, Engine oil, pump operator, labour charges, conveyance of pumpset and fuel to site and back, loading, unloading and any other incidental charges etc., complete and as direced by the TWAD Board Officers. | 14 | hour | Special specifications | one hour
iii) | Supply and delivery of 500mm MS Cut barrel at the site of work including at the site of work etc. complete as directed by TWAD Board Officers without inside lining and outside coating but with antirust painting | 84.19 | Kg | Special specifications | one Kg
6) | Attending Leak works in the Pumping main of 600mm MS Pipe
i) | Earth work excavation and depositing on bank in hard stiff clay, stiff black cotton soil, hard red earth, shales, murrams, ordinary gravel stoney earth mixed with small sized boulders etc., for leak rectification works for the following sizes of Pipes and as directed by TWAD Bd. Officers | 76.21 | m3 | SS 20 B,23, 95 and Special specifications | One Cubic metre
ii) | Dewatering using 5HP diesel engine pumpset including Hire charges, cost of Diesel, Engine oil, pump operator, labour charges, conveyance of pumpset and fuel to site and back, loading, unloading and any other incidental charges etc., complete and as direced by the TWAD Board Officers. | 112 | hour | Special specifications | one hour
iii) | Supply and delivery of 500mm MS Cut barrel at the site of work including at the site of work etc. complete as directed by TWAD Board Officers without inside lining and outside coating but with antirust painting | 707.65 | Kg | Special specifications | one Kg
7) | Attending burst works in GI pipe
i) | Supply and delivery of GI Pipes confirmation to IS inclusive of transportation charges anywhere in Tamil nadu etc complete and as directed by TWAD Board officers |  |  | IS 1239/PART I/2004
a) | 40 mm GI pipe | 4 | m |  | one metre
b) | 50 mm GI pipe | 22 | m |  | one metre
c) | 80 mm GI pipe | 4 | m |  | one metre
ii | Supply and deliery of PVC specials confirmation to IS inclusive of transportation charges anywhere in Tamil nadu etc complete and as directed by TWAD Board officers |  |  | IS 10124/1982 Part-II
a) | 50 mm PVC Male Threaded Adopter | 4 | Nos |  | Each
b) | 63 mm PVC Male Threaded Adopter | 22 | Nos |  | Each
c) | 80 mm PVC Male Threaded Adopter | 4 | Nos |  | Each
iii) | Lowering of GI Pipes and specials in the trenches and laying to proper grade and alignment and as directed by the TWAD Officers |  |  | Special specifications
a) | 40 mm GI pipe | 4 | m |  | one metre
b) | 50 mm GI pipe | 22 | m |  | one metre
c) | 80 mm GI pipe | 4 | m |  | one metre
8) | Carrying out the following repair works occuring during the maintenance period in the Electrical, Mechanical and Elctro-mechanical items to bring back the scheme / components into normal running conditition as per standard specification including all labour charges, cost of materials and all incidental charges within the stipulated time limit etc., complete as specified in Clause 2.2.6 of General conditions of Contract Part II etc as directed by TWAD Board officers
a) | Rewinding of motor and reconditioning of pump and repair works including ost of all materials, conveyance charges, labour charges for removing and re-erection of Submersible pumpsets for the following Booster stations for wayside sumps |  |  | Special Specification
i) | 1 HP | 6 | Job |  | Each job
ii) | 1.5 HP | 2 | Job |  | Each job
iii) | 2.0 HP | 2 | Job |  | Each job
iv) | 3.0 HP | 2 | Job |  | Each job
v) | 5 HP | 1 | Job |  | Each job
vi) | 7.5 HP | 2 | Job |  | Each job
vii) | 10 HP | 1 | Job |  | Each job
b) | Rewinding of motor and reconditioning of pump and repair works including ost of all materials, conveyance charges, labour charges for removing and re-erection of HSC pumpsets for the following Booster stations for wayside sumps |  |  | Special Specification
i) | 10 HP | 1 | Job |  | Each job
ii) | 12.5 HP | 1 | Job |  | Each job
iii) | 15 HP | 1 | Job |  | Each job
iv) | 20 HP | 1 | Job |  | Each job
v) | 25 HP | 1 | Job |  | Each job
vi) | 50 HP | 1 | Job |  | Each job
vii) | 75 HP | 1 | Job |  | Each job
viii | 100 HP | 1 | Job |  | Each job
c) | Rewinding of motor and reconditioning of Motor and repair works including ost of all materials, conveyance charges, labour charges for removing and re-erection of Vertical Turbine pumpsets for the following Booster stations for wayside sumps |  |  | Special Specification
i) | 120 HP | 1 | Job |  | Each job
d) | Repair and reconditioning works in HSC centrifugal Pump including cost of all material exluding Bronze impeller ,conveyance ,labour charges for removing and re-erection of centrifugal HSC Pump |  |  | Special Specification
i) | 10 HP | 1 | Job |  | Each job
ii | 12.5 HP | 1 | Job |  | Each job
iii) | 15 HP | 1 | Job |  | Each job
iv) | 20 HP | 1 | Job |  | Each job
v | 25 HP | 1 | Job |  | Each job
vi | 50 HP | 1 | Job |  | Each job
vii) | 75 HP | 1 | Job |  | Each job
viii | 100 HP | 1 | Job |  | Each job
e) | Repair and reconditioning works in Vertical Turbine pump including cost of all material exluding Bronze impeller ,conveyance ,labour charges for removing and re-erection of Vertical Turbine pump |  |  | Special Specification
i) | 120 HP Vertical Turbine Pump | 1 | Job |  | One job
f) | SUPPLY AND DELIVERY OF OVER LOAD RELAY |  |  | Special Specification
i) | Supply and delivery of Directly operated Bimetallic Thermal overload relay Upto 5A-10A which operates in case of overload and also in case of under voltage with manual and auto reset mode | 26 | Job |  | Each job
ii | Supply and delivery of Directly operated Bimetallic Thermal overload relay Upto 10A-20A which operates in case of overload and also in case of under voltage with manual and auto reset mode | 7 | Job |  | Each job
iii) | Supply and delivery of Directly operated Bimetallic Thermal overload relay Upto 20A-30A which operates in case of overload and also in case of under voltage with manual and auto reset mode | 4 | Job |  | Each job
iv) | Supply and delivery of Directly operated Bimetallic Thermal overload relay Upto 50A-75A which operates in case of overload and also in case of under voltage with manual and auto reset mode | 1 | Job |  | Each job
v | Supply and delivery of Directly operated Bimetallic Thermal overload relay Upto 75A-110A which operates in case of overload and also in case of under voltage with manual and auto reset mode | 1 | Job |  | Each job
vi | Supply and delivery of Directly operated Bimetallic Thermal overload relay Upto 150A-200A which operates in case of overload and also in case of under voltage with manual and auto reset mode | 2 | Job |  | Each job
vii) | Supply and delivery of Directly operated Bimetallic Thermal overload relay Upto 200A-300A which operates in case of overload and also in case of under voltage with manual and auto reset mode | 1 | Job |  | Each job
g) | SUPPLY AND DELIVERY OF ELECTROMAGNETCI CONTACTORS |  |  | Special Specification
viii | Supply and delivery of 16 Amps\440V Electro magnetic Contactors Suitable for Starter in AC Three Phase rating Conforming to IS/IEC 60947-4-1 | 5 | Job |  | Each job
ix | Supply and delivery of 18 Amps\440V Electro magnetic Contactors Suitable for Starter in AC Three Phase rating Conforming to IS/IEC 60947-4-1 | 15 | Job |  | Each job
x | Supply and delivery of 25 Amps\440V Electro magnetic Contactors Suitable for Starter in AC Three Phase rating Conforming to IS/IEC 60947-4-1 | 12 | Job |  | Each job
xi | Supply and delivery of 32 Amps\440V Electro magnetic Contactors Suitable for Starter in AC Three Phase rating Conforming to IS/IEC 60947-4-1 | 2 | Job |  | Each job
xii | Supply and delivery of 40 Amps\440V Electro magnetic Contactors Suitable for Starter in AC Three Phase rating Conforming to IS/IEC 60947-4-1 | 5 | Job |  | Each job
xiii | Supply and delivery of 70 Amps\440V Electro magnetic Contactors Suitable for Starter in AC Three Phase rating Conforming to IS/IEC 60947-4-1 | 2 | Job |  | Each job
xiv | Supply and delivery of 95 Amps\440V Electro magnetic Contactors Suitable for Starter in AC Three Phase rating Conforming to IS/IEC 60947-4-1 | 2 | Job |  | Each job
xv | Supply and delivery of 140 Amps\440V Electro magnetic Contactors Suitable for Starter in AC Three Phase rating Conforming to IS/IEC 60947-4-1 | 2 | Job |  | Each job
xvi | Supply and delivery of 400 Amps\440V Electro magnetic Contactors Suitable for Starter in AC Three Phase rating Conforming to IS/IEC 60947-4-1 | 2 | Job |  | Each job
h) | Attending Cable fault for Infiltration Well and Head works Pump room. |  |  | Special specifications
i | Supply, delivery of 1.1 KV Grade PVC insulated and steel Armoured aluminium cable etc complete directed by the TWAD Board officers
a | 3 core 95 Sq. mm aluminium cable | 32 | m |  | One Metre
b | 3.5core 400 Sq. mm aluminium cable | 12 | m |  | One Metre
ii | Laying of 1.1 KV Grade PVC insulated steel Armoured aluminium cable as per I.E. rules etc complete directed by the TWAD Board officers
a | 3 core 95 Sq. mm aluminium cable | 32 | m |  | One Metre
b | 3 core 400 Sq. mm aluminium cable | 12 | m |  | One Metre
iii) | Jonting the 1.1KV grade PVC Insulated Steel armoured aluminum cable as per I E Rules including Jointing materials etc complete directed by the TWAD Board officers
a | 3 core 95 Sq. mm aluminium cable | 2 | Joint |  | Each Joint
b | 3 core 400Sq. mm aluminium cable | 2 | Joint |  | Each Joint
iv) | Supply, delivery of 1.1 KV Grade PVC insulated and steel Armoured aluminium cable etc complete directed by the TWAD Board officers
a | 3 core 35 Sq. mm aluminium cable | 550 | m |  | One Metre
a | 3 core 90 Sq. mm aluminium cable | 550 | m |  | One Metre
v | Laying of 1.1 KV Grade PVC insulated steel Armoured aluminium cable as per I.E. rules etc complete directed by the TWAD Board officers
a | 3 core 35 Sq. mm aluminium cable | 550 | m |  | One Metre
a | 3 core 90 Sq. mm aluminium cable | 550 | m |  | One Metre
vi | Jonting the 1.1KV grade PVC Insulated Steel armoured aluminum cable as per I E Rules including Jointing materials etc complete directed by the TWAD Board officers
a | 3 core 35 Sq. mm aluminium cable | 6 | Joint |  | Each Joint
a | 3 core 90 Sq. mm aluminium cable | 6 | Joint |  | Each Joint
i) | Supply and delivery of following Range AMPS 3 Pole MCCB Switch ( Moulted case circuit breakers) to control EB supply from E.B Pole to Main Panel Board |  |  | Special specifications
i) | 32 Amps 3 Pole MCCB Switch | 1 | Nos |  | Each
ii) | 63 Amps 3 Pole MCCB Switch | 2 | Nos |  | Each
iii) | 100 Amps 3 Pole MCCB Switch | 3 | Nos |  | Each
iv) | 160 Amps 3 Pole MCCB Switch | 2 | Nos |  | Each
v | 200 Amps 3 Pole MCCB Switch | 1 | Nos |  | Each
vi | 320 Amps 3 Pole MCCB Switch | 2 | Nos |  | Each
vii | 250 Amps 3 Pole MCCB Switch | 1 | Nos |  | Each
viii | 400 Amps 3 Pole MCCB Switch | 1 | Nos |  | Each
j) | Supply and delivery of direct online starter confirming to IS13947 and IEC60947-1 suitable KW rating for operation in AC/ three Phase/50HZ(+/- 5%) and 415V (+/- 10%) including Ammeter, Overload relay, under Voltage release with no Volt coil, Air Break contactors suitable for next Standard higher KW rating, Single phasing preventor, dry running preventor and On/Off Push button switches, including the capacitor(the cost of capacitor is to be taken separately). |  |  | IS13947 and IEC60947-1 & Special specifications
1 | 1 Hp | 1 | Nos |  | Each
2 | 1.5 HP | 1 | Nos |  | Each
3 | 2 HP | 1 | Nos |  | Each
4 | 3HP | 1 | Nos |  | Each
5 | 5HP | 1 | Nos |  | Each
k) | Supply and delivery Power capacitor for power factor improvement with oil filled with discharge resistance 3 phase 415/440V 50 HZ conforming to ISS:2834 with ISI marking | 231 | KVAR |  | Each KVAR
9)a) | Repairing/ reconditioning of Sluice valve (for line valve/ for Scour valve) including all material, labour (Specify type of sluice valve and type of repair to be carried out) |  |  | Special specifications
1 | 80 mm CI Sluice valve | 5 | Nos |  | Each
2 | 100 mm CI Sluice valve | 10 | Nos |  | Each
3 | 125 mm CI Sluice valve | 2 | Nos |  | Each
4 | 150 mm CI Sluice valve | 1 | Nos |  | Each
5 | 200 mm CI Sluice valve | 1 | Nos |  | Each
6 | 250 mm CI Sluice valve | 2 | Nos |  | Each
7 | 300 mm CI Sluice valve | 2 | Nos |  | Each
8 | 500 mm CI Sluice valve | 3 | Nos |  | Each
9 | 600 mm CI Sluice valve | 5 | Nos |  | Each
10 | 40 mm CI NRV valve | 7 | Nos |  | Each
11 | 50 mm CI NRV valve | 3 | Nos |  | Each
12 | 65 mm CI NRV valve | 5 | Nos |  | Each
13 | 80 mm CI NRV valve | 1 | Nos |  | Each
14 | 100 mm CI NRV valve | 12 | Nos |  | Each
15 | 125 mm CI NRV valve | 1 | Nos |  | Each
16 | 150 mm CI NRV valve | 1 | Nos |  | Each
17 | 200 mm CI NRV valve | 1 | Nos |  | Each
18 | 250 mm CI NRV valve | 1 | Nos |  | Each
19 | 300 mm CI NRV valve | 4 | Nos |  | Each
20 | 50mm Air valve | 15 | Nos |  | Each
21 | 80 mm Air valve | 10 | Nos |  | Each
22 | 100 mm Air valve | 10 | Nos |  | Each
23 | 150 mm Air valve | 15 | Nos |  | Each
9) b | Supply, delivery and fixing of following size of Gate valves in OHT's and Pumproom |  |  | Special specifications
a) | 40 mm Gate valve | 18 | Nos |  | Each
b) | 50 mm Gate valve | 11 | Nos |  | Each
c) | 65 mm Gate valve | 15 | Nos |  | Each
10 | Removal of sediments and depositions of sludge, silt particles inside the sump at various capacities by engaging required labours and diesel pumpsets and cleaning the sidewall and bottom of sump using wirebrushes, brooms, collecting, lifting of the deposited silt particles outside the sump, washing side wall and floor slab using bleaching powdre etc complete and as directed by TWAD Board officers |  |  | Special specifications
a) | 9.00 LL | 1 | Nos |  | Each
b) | 9.00 LL | 1 | Nos |  | Each
c) | 8.00 LL | 2 | Nos |  | Each
d) | 7.00 LL | 1 | Nos |  | Each
e) | 4.00 LL | 3 | Nos |  | Each
f) | 3.00 LL | 1 | Nos |  | Each
g) | 2.00 LL | 1 | Nos |  | Each
h) | 1.50 LL | 5 | Nos |  | Each
i) | 1.00 LL | 8 | Nos |  | Each
j) | 0.60 LL | 7 | Nos |  | Each
k) | 0.30 LL | 7 | Nos |  | Each
l) | 0.10 LL | 4 | Nos |  | Each
11 | Desilting light or sandy soil or silt from infiltration wells below water level including the charges for special tools and plants and air compressor etc.complete and as directed by the TWAD Board Officers.- 16 nos. | 127.2 | m3 | Special specifications | One Cubic metre
| Total | [6 empty] | 0