# SALIENT DETAILS

| 1 | ### Name of Scheme | ### CWSS to 7 Town Panchayats and 395 Raural Habitations in Srivilliputhur, Rajapalayam and Watrap Unions in Virudhunagar District with Thamirabarani River as Source Near Mukkudal. |
| --- | --- | --- |
| 2 | Details of Sanction: |  |
| a) | Administrative Sanction | G.O.(MA &WS) No: 166 dt 11.08.2010 for Rs.173.00Crores |
| b) | Technical Sanction | CE / SR /MDU:No: 76 /TWAD/2010-2011/ dated 27.12.2010 for Rs.170.00Crores |
| 3 | ### Maintenance Cost | Rs.580.00 Lakhs. |
| 4 | ### Per capita cost present (2012) | Rs.4423 |
| 5 | ### Cost per 1000 Litre. | Rs.21.30 |

- POPULATION:

Number of Habitations and   populations     to cover in this reach is detailed below.

| Sl.No. | Name of Unios | No.Of Habitations | Censes Population 2001 | Present Population 2012. | Intermediate Population 2027. | Ultimate Population 2042. |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Srivilliputhur | 161 | 78308 | 83245 | 91579 | 99894 |
| 2 | Watrap | 82 | 68042 | 72458 | 79706 | 86950 |
| 3 | Rajapalayam | 147 | 107975 | 114739 | 126221 | 137687 |
| 4 | Sivakasi | 5 | 1761 | 1873 | 2060 | 2247 |
|  | Total Rural Habitations | 395 | 256086 | 272315 | 299566 | 326778 |
| 5 | Town Panchayats | 7 | 93331 | 112000 | 131600 | 155000 |
|  | Total Habs | 402 | 349417 | 384315 | 431166 | 481778 |

7. WATER DEMAND

| Sl. No. | Description | Water Requirement |  |
| --- | --- | --- | --- |
|  |  | Intermediate 2027 | Ultimate 2042 |
| a | Population |  |  |
|  | Rural Habitations | 299566 | 326778 |
|  | Town Panchayats | 131600 | 155000 |
|  | Total | 431166 | 481778 |
| b | Prorate supply |  |  |
|  | Rural Habitations | 30 lpcd | 30 lpcd |
|  | Town Panchayats | 70 lpcd in total(including existing supply in summer) | 70 lpcd total |
| c | Requirement in lpm for 23 hrs of Pumping and minimum 10 lpm |  |  |
|  | For 395 Rural Habitations | 7235 | 7886 |
|  | For 7 Town Panchayats | 3971 | 5277 |
|  | Total requirement in lpm | 11206 | 13163 |
| d | Requirement in lit/day(including Transmission loss 10 % ) | 15.46 MLD | 18.16 MLD |
| e | Hours of Pumping |  | For Main 23 Hrs and for rural 12 Hrs |

| 8. | ### Components |  |
| --- | --- | --- |
| ### I | ### HEAD WORKS |  |
| ### A. | ### Source | Sub surface water from Thamirabarani River near Mukkudal (13 nos of Infiltration wells of 4.5 m dia ) |
| ### B. | ### Quantity drawal from each well | 862 lpm in intermediate year, 1012 lpm in Ultimate period. |
| ### C. | ### 1).Common Sump 2).Pump Room 3).P’set a.Infiltration well b. Common sump 4).Compound wall | 8.00 LL Capacity -1no 15mx9m-1no 862lpmx18m Head -13 nos with 100% standby HSC pump set ,5603 lpmx 76m Head – 3 nos (two nos. running in Parallel to discharge 11206 lpmx76m head, with 50 % standby) 50mx50m -1no. |

8.II). INTERMEDIATE BOOSTERS:

1.

| A. | Booster @ Maruthamputhur |  |
| --- | --- | --- |
|  | 1.Common Sump 2.Pump Room 3.Pumpset 4.Compound wall | 8.00 LL 12mx 8m HSC pump set ,5603 lpmx 62m Head – 3 nos (two nos. running in Parallel to discharge 11206 lpmx62m head, with 50 % standby) 50mx50m – 1no |
| B. | Booster @ Uthumalai |  |
|  | 1.Common Sump 2.Pump Room 3.Pumpset 4.Compound wall | 8.00 LL 12mx 8m HSC pump set ,5603 lpmx 73m Head – 3 nos (two nos. running in Parallel to discharge 11206 lpmx73m head, with 50 % standby) 50mx50m – 1no |
| C. | Booster @ Perumalpatti Villaku |  |
|  | 1.Common Sump 2.Pump Room 3.Pumpset 4.Compound wall | 8.00 LL 12mx 8m HSC pump set ,4013 lpmx 14m Head –3 nos (two nos. running in Parallel to discharge 8026 lpmx14m head, with 50 % standby) & Submersible P’set – 3181 lpmx51m -2nos with 100 % standby) 50mx50m – 1no |

2).Capacity of sumps at Boosters including Head works and Rural sumps and Town Panchayat

Sumps

| Capacity | Srivilliputhur | Watrap | Sivakasi | Rajapalayam | Town Panchayat | Total |
| --- | --- | --- | --- | --- | --- | --- |
| 15000 Lit |  |  |  | 1 |  | 1 |
| 20000 Lit |  | 1 |  | 1 |  | 2 |
| 25000 Lit |  | 5 |  | 2 |  | 7 |
| 30000 Lit | 1 |  | 1 | 1 |  | 3 |
| 35000 Lit | 2 | 2 |  | 1 |  | 5 |
| 40000 Lit | 1 | 2 |  | 2 |  | 5 |
| 45000 Lit | 5 | 2 |  | 2 |  | 9 |
| 50000 Lit | 1 | 1 |  | 2 |  | 4 |
| 55000 Lit |  | 1 |  | 3 |  | 4 |
| 60000 Lit | 6 |  |  | 1 |  | 7 |
| 65000 Lit | 2 |  |  | 1 | 1 | 4 |
| 70000 Lit | 1 |  |  | 1 |  | 2 |
| 75000 Lit | 2 |  |  | 2 |  | 4 |
| 80000 Lit |  | 1 |  | 1 |  | 2 |
| 85000 Lit | 1 | 1 |  | 2 |  | 4 |
| 90000 Lit |  | 3 |  | 3 |  | 6 |
| 95000 |  | 1 |  | 2 |  | 3 |
| 100000 Lit | 2 | 1 |  | 2 |  | 5 |
| 105000 Lit | 2 |  |  | 1 |  | 3 |
| 110000 Lit |  |  |  |  | 1 | 1 |
| 115000 Lit |  | 1 |  |  |  | 1 |
| 145000 Lit |  | 1 |  |  |  | 1 |
| 150000 Lit |  |  |  | 2 | 1 | 3 |
| 155000 Lit |  |  |  | 1 |  | 1 |
| 170000 Lit |  | 1 |  |  |  | 1 |
| 175000 Lit | 1 |  |  |  |  | 1 |
| 180000 Lit |  |  |  |  | 2 | 2 |
| 280000 Lit |  |  |  |  | 1 | 1 |
| 310000 Lit |  |  |  | 1 |  | 1 |
| 315000 Lit |  |  |  |  | 1 | 1 |
| 390000 Lit |  | 1 |  |  |  | 1 |
| 415000 Lit | 1 |  |  |  |  | 1 |
| Capacity | Srivilliputhur | Watrap | Sivakasi | Rajapalayam | Town Panchayat | Total |
| 505000 Lit | 1 |  |  |  |  | 1 |
| 520000 Lit | 1 |  |  |  |  | 1 |
| 565000 Lit |  |  |  | 1 |  | 1 |
| 800000 Lit(H.W-1no+IB-3nos) |  |  |  |  |  | 4 |
| TOTAL | 30 | 25 | 1 | 36 | 7 | 103 |

3). PUMPHOUSES:

Pump  houses   are  proposed in   all  sump sites   to accommodate  the   HSC  pump  sets  and  panel boards  and  panel  boards of  submersible pump sets.  The   size is fixed based on the number   and   type  of pump set.s.  Pump room of  size    from      15.00m  X 9.00 m to 2.0 m X2.0 m have been proposed.

| Size of P;Room | HW | Intermediate booster | Watrap Union | Srivilliputhur Union | Rajapalayam Union | Sivakasi Union | Town Panchayat | Total nos. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2.0 M X 2.0 M | -- | -- | 19nos | 21nos | 29nos | 1no | 7nos | 77 nos |
| 3.0 M X 3.0 M | -- | -- | 3nos | 5nos | 1no | -- |  | 9 nos |
| 4.0 M X 3.0 M | -- | -- | 1no | 1nos | 4nos | -- |  | 6 nos |
| 6.0 M X 4.0 M | -- | -- | 1no | -- | 1no | -- |  | 2 nos |
| 8.0 M X 5.0 M | -- | -- | 1no | 3nos | 1no | -- |  | 5 nos |
| 12.0 M X 8.0 M | -- | 3 nos | -- | -- | -- | -- |  | 3 nos |
| 15.0 MX9.0 M | 1nos | -- | -- | -- | -- | -- |  | 1 nos |
| Total | 1no | 3nos | 25nos | 30nos | 36nos | 1no | 7nos | 103nos |

4.. PUMPSET:

For head works and booster stations, at Maruthamputhur, Uthumalai, , PerumalpattiVilakku,  Gopalapuram,,Ramachandrapuram Vilakku, Malli and Pattakkulam, 7Horizontal                                                                                                                                                                                      split casing centrifugal pump sets  with positive head have been proposed  with 50% standby. For other main pumping stations , open well  submersible pump sets are proposed with 100% stand bye. And for rural sump also  open well submersible pump sets are proposed with 100% stand bye. HSC pumpsets of  250 HP to 35 HP and  open well submersible pumpsets of 50HP to 1HP  are proposed in this project at   sumps depending upon the discharge and head , to pump water from main sump to rural sumps and rural sumps to OHTs in the Habitations.

8.III). PUMPING MAIN AND BRANCH MAINS :

The pipe proposed for pumping main and branch feeder main are as  detailed below.

600mm to 150 mm DI K7 pipes                                        – 164.81 KM

160mm OD PVC 6 Ksc to 50mm OD PVC 6 Ksc               - 203.53 KM

125MM dia to 40mm dia GI pipes for Canal/ Odai crossing -   9.07 KM

Net total 					              - 377.41 KM

8.IV).PUMPING AND BRANCH MAINS TO ALL RURAL HABITATIONS

140mm OD PVC 6Ksc , 4 KSC to 50mm6 KSC – 410.930 km

8.V). INFRASTRUCTURE   TO RURAL HABITATIONS

I.SERVICE RESERVOIR

1. 10000 LIT OHT 		-  14nos.

2. 20000 LIT OHT		-    1 nos

TOTAL			- 15 nos.

II. DISTRIBUTION SYSTEM

63MM OD PVC PIPE 		-  6.30 km

single tap pf			- 23 nos.

III. Inlet Connection to Exixting OHTs – 380 Habitations.

INFRASTRUCTURE TO TOWN PANCHAYATS.

1.Seithur TP

D’ system -  1.0 km

2. Chettiyarpatti TP –

D’ system -  5.60 km

3. Mamsapuram TP  –

3.0 LL OHT – 1no.

D’system –  9.05 km

4. Sundarapandiam -

D’system – 2.40 km

5.W.Pudupatti TP

D’system – 1.80 km

6.Watrap

D’system – 1.5km.

7. S.Kodikulam

D’system – 5.0 km