SALIENT DETAILS

| Name of Scheme | CWSS to 755 rural habitations in Sattur, Vembakottai, Virudhunagar, Sivakasi, Watrap(Part), Srivilliputhur(Part) and Aruppukottai(Part) unions in Virudhunagar District with River Thamirabarani as Source near Seevalaperi including maintenance period of 12 months. |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Installation Cost | Rs. 234.00Crore. |  |  |  |  |  |  |  |  |  |  |  |
| A.M.Cost | Rs. 8.20 Crore. |  |  |  |  |  |  |  |  |  |  |  |
| Per capita cost | Rs. 4310.00/- |  |  |  |  |  |  |  |  |  |  |  |
| Cost per 1000 litres | Rs. 21.11 |  |  |  |  |  |  |  |  |  |  |  |
| Proportionate installation Cost & AM cost | Name of Beneficiary |  |  |  |  | Installation Cost (Rs. in Crore) |  |  |  |  | A. M. Cost (Rs. in Crore) |  |
|  | 755 Rural Habitations |  |  |  |  | 234.00 |  |  |  |  | 8.20 |  |
| POPULATION AND REQUIREMENT DETAILS |  |  |  |  |  |  |  |  |  |  |  |  |
| Name of Beneficiary |  | Population |  |  |  |  | Net Demand (in mld) |  |  |  |  |  |
|  |  | Base Year (2012) | Intermediate (2027) |  | Ultimate (2042) |  | Base Year (2012) |  |  | Intermediate (2027) |  | Ultimate (2042) |
| #### Virudhunagar Union |  | 149671 | 164646 |  | 179602 |  | 5.05 |  |  | 5.54 |  | 6.04 |
| #### Sivakasi Union |  | 175584 | 193152 |  | 210703 |  | 5.79 |  |  | 6.37 |  | 6.95 |
| #### Sattur Union |  | 112632 | 123905 |  | 135155 |  | 3.72 |  |  | 4.09 |  | 4.46 |
| #### Vembakottai Union |  | 91087 | 100204 |  | 109299 |  | 3.01 |  |  | 3.31 |  | 3.61 |
| #### Aruppukottai union |  | 11418 | 12560 |  | 13702 |  | 0.38 |  |  | 0.42 |  | 0.45 |
| #### Watrap Union (Part) |  | 320 | 352 |  | 384 |  | 0.01 |  |  | 0.01 |  | 0.01 |
| #### Srivilliputhur Union ( Part) |  | 2192 | 2411 |  | 2630 |  | 0.07 |  |  | 0.08 |  | 0.09 |
| #### Grand Total |  | 543163 | 597230 |  | 651475 |  | 18.03 |  |  | 19.82 |  | 21.61 |
| Total Quantity after including 10% transmission loss ( in mld) |  |  |  |  |  |  | 18.03 |  |  | 19.82 |  | 21.61 |
| Components of scheme: |  |  |  |  |  |  |  |  |  |  |  |  |
| Source |  |  |  | Surface water from Thamirabarani River near Seevalaperi to be drawn through offtake pipe (gravity main) of 800mm DI and Collected in a collection sump cum Pump house (Check dam at the site to be constructed by PWD as deposit work) |  |  |  |  |  |  |  |  |
| Head works |  |  |  | Check Dam |  |  |  | 390m |  |  |  |  |
|  |  |  |  | Offtake well |  |  |  | 1No |  |  |  |  |
|  |  |  |  | Gravity main- 800mm DI K7 pipe |  |  |  | 500 mts |  |  |  |  |
|  |  |  |  | Raw water Sump cum Pump house |  |  |  | 1 No |  |  |  |  |
|  |  |  |  | Vertical Turbine Pump set |  |  |  | 3 nos |  |  |  |  |
|  |  |  |  | Connecting Main – 600mm DI K7 pipe |  |  |  | 700 mts |  |  |  |  |
| Treatement Plant |  |  |  | Full scale Treatment plant at Seevalaperi– 21.00 MLD |  |  |  |  |  |  |  |  |
| Booster Pumping Stations |  |  |  | At Rajapudukudi - 9.50 LL At Savalaperi - 9.50 LL At UppathurVilakku -11.55 LL At Naduvapatti - 3.35 LL At Pavalivilakku - 2.05 LL |  |  |  |  | 5 Nos. |  |  |  |
| Pumping main & Feeder main |  |  |  | 712mm MS pipe (6mm Thick) |  |  |  |  | 65.774 KM |  |  |  |
|  |  |  |  | From 600mm DI K7 pipe to 200mm K7 pipe |  |  |  |  | 123.213 KM |  |  |  |
|  |  |  |  | PVC pipes 160mm to 50mm PVC 6ksc pipe |  |  |  |  | 1335.013 KM |  |  |  |
| Rural Sumps & pump Rooms |  |  |  | Rural Sumps Pump Room |  |  |  |  | 157 Nos. 157 Nos. |  |  |  |
| Pump sets for Rural |  |  |  | HSC Pump sets. |  |  |  |  | 23 Nos |  |  |  |
|  |  |  |  | Submersible |  |  |  |  | 429 Nos |  |  |  |
| Service Reservoir |  |  |  | Rural Areas |  |  |  |  | 7 Nos |  |  |  |